Work Paper SCE13HC029

Revision 3

Southern California Edison Company

Residential HVAC Quality Maintenance

# At-a-Glance Summary

| Applicable Measure Codes: | AC-44078, AC-56069, AC-95345, AC-94699, AC-60036, AC-21964, AC-16390 |
| --- | --- |
| Measure Description: | HVAC Quality Maintenance treatments: Refrigerant charge adjustment, condenser coil cleaning, evaporator coil cleaning, air flow adjustment, duct seal medium to low, duct seal high to low, and design capacity sizing |
| Base Case Description: | Central air-cooled direct expansion cooling and gas heating without adequate Quality Maintenance |
| Energy Impact Common Units: | Ton |
| Energy Savings : | Refer to Excel Calculation Attachment |
| Gross Measure Cost ($/unit) | Refer to Excel Calculation Attachment |
| Measure Incremental Cost ($/unit): | Refer to Excel Calculation Attachment |
| Effective Useful Life (years): | 5 years |
| Measure Application Type: | Retrofit Add-On (REA), Replace-on-Burnout (ROB) |
| Net-to-Gross Ratios: | 0.85 |
| Important Comments: | This work paper document does not contain a data set in conformance with the 4/1/14 CPUC Ex Ante Database Specification; SCE will provide that data set separately. This work paper uses savings values from the May 2, 2013 Energy Division Workpaper Disposition for Residential HVAC Quality Maintenance. |

# Document Revision History

| Workpaper and Revision # | Tech. Revision | MM/DD/YY | Author/Affiliation | Summary of Changes |
| --- | --- | --- | --- | --- |
| SCE13HC029.0 | No | 05/29/2012 | Janice Peterson, PECI | Original work paper |
| SCE13HC029.1 | No | 12/04/2013 | Ryan Cho/SCE | In accordance with the Energy Division’s disposition [34], the following revisions are incorporated into this workpaper. - Revised all Unit Energy Savings (UES) values. - Updated the EUL value to 5 years. - Updated the solution codes. |
| SCE13HC029.2 | No | 12/31/2013 | Yun Han/SCE | - Updated to latest WP template - Add Residential Mobile Home – Double-Wide building type - Add Direct Install Delivery & Incentive Method - Update NTG for Direct Install and Downstream |
| SCE13HC029.3 | Yes | 5/09/2014 | Andres Fergadiotti/SCE | - Work paper updated for the reporting period, effective 7/1/14 – 12/31/14. - Updated DMH savings - Removed Brushless Direct Current Blower Motor measure, which is addressed in SCE13HC028 (Solution Code: AC-68273 ) |
|  |  | 7/30/2014 | Andres Fergadiotti/SCE | - The single Res HVAC QM measure was broken out into multiple measures, in alignment with PG&E. - Measure savings are from the 5/2/13 ED Res QM Disposition. - Some disposition savings were replaced with newer DEER2014 values: Res-RefrigCharge-wtd, Res-DuctSeal-HighToLow-wtd, and Res-DuctSeal-MedToLow-wtd - Added new measure “Design Capacity Sizing.” - Updated all costs |

# Section 1. General Measure & Baseline Data

## 1.1 Measure Description & Background

This work paper details the Residential HVAC Quality Maintenance (QM) measures for packaged and split system HVAC units. These treatments are related to ductwork and HVAC unit optimization; see Table 1.

Table 1 Measure Names

| Solution Code | Measure name |
| --- | --- |
| AC-44078 | Refrigerant Charge Adjustment |
| AC-56069 | Condenser Coil Cleaning |
| AC-95345 | Evaporator Coil Cleaning |
| AC-94699 | Air Flow Adjustment |
| AC-60036 | Duct Seal Med to Low |
| AC-21964 | Duct Seal High to Low |
| AC-16390 | Design Capacity Sizing |

Measure Requirements

Residential Single Family, Multi-family, and Double-wide Mobile Homes in SCE’s climate zones that use central air-cooled direct expansion cooling and gas heating are eligible. The participant must have electricity distributed by Southern California Edison (SCE) to the installation service address. Additionally, the following prerequisites must be met before the Quality Maintenance measures can be implemented:

- Unit and system must be capable of delivering a supply air flow rate of at least 350 cfm/ton after treatments related to airflow are completed and before refrigerant charge is tested and/or adjusted.

- Unit must be drawing power.

- Unit must have a condenser over ambient temperature (COAT) of at least 3 degrees.

- Customer must agree to QM Service Agreement.

The 350 cfm/ton airflow requirement ensures that the refrigerant system can be properly diagnosed and charged. If the system is not delivering 350 cfm/ton upon initial inspection, an assessment should be made to determine if the system will be able to deliver 350 cfm/ton by implementing some or all of the QM treatments related to airflow. If it is determined that the supply fan and duct system in place do not have the capability to deliver 350 cfm/ton after the airflow treatments have been performed, refrigerant charge cannot be properly diagnosed, rendering the QM process incomplete and the savings in this work paper invalid.

If some or all of the existing ductwork is beyond repair and sections must be replaced, the sections that must be replaced must be less than 40 linear feet in total per 2013 Title 24 Section 150.2(b), or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2013 Title 24 Section 150.2(b)1D [355].

The level of maintenance by technicians on a typical air conditioner unit is minimal with service being performed at an unacceptable level. This may eventually lead to unit failure and/or poor performance, forcing premature equipment replacement. In response to this problem, Air Conditioner Contractors of America (ACCA) developed Standard 4 for “Maintenance of Residential HVAC Systems” [1]. For the measures contained in this work paper, an assessment and report is required in accordance with ACCA Standard 4 prior to any treatments being applied to determine the baseline conditions and to develop treatment recommendations.

## Technical Description

Proper maintenance of the unit enables an air conditioner to operate at or near its optimal efficiency. The Quality Maintenance measures are treatments designed to increase the unit’s ability to deliver heating and cooling efficiently and to provide increased thermal comfort.  An example of a performance/parameter improvement is: Refrigerant Charge Adjustment improves EER and Cooling Capacity. Table 8 provides details for all treatments.

The Design Capacity Sizing measure, not included in the ED Disposition or DEER2014 database, is intended to address oversizing of the Design (Cooling) Capacity of the base case mechanical (HVAC) system, generally in the order of 20% over a properly sized mechanical system as documented and suggested in the SCE’s Residential Quality Installation workpaper (SCE13HC023). This is an ROB measure because the customer’s existing equipment has passed its useful life, and the customer has the opportunity to choose a properly sized system as the replacement.

## 1.3 Measure Application Type

The delivery methods are:

- Financial Support – Downstream Incentive – Deemed

- Financial Support – Direct Install.

The install types are:

- Replace-on-Burnout (ROB) for Design Capacity Sizing

- Retrofit Add-on (REA) for the remaining measures

## 1.4  Measure and Base Case Cost Effectiveness Data

### 1.4.1 DEER Measure and Base Case Analysis

DEER 2014 contains some of the QM treatments as standalone measures, with the assumption that all other features of the prototype are held constant at an energy efficient baseline; the standalone measures are: refrigerant charge and adjustment, duct sealing, refrigerant charge with duct sealing, and commercial condenser coil cleaning. To determine savings, DEER values were modified as shown in the 5/2/13 ED Residential HVAC QM Disposition.

Table 2 DEER Difference Summary

| DEER Difference Summary Table |  |
| --- | --- |
| Modified DEER Methodology | Yes |
| Scaled DEER Measure | No |
| DEER Building Prototypes Used | No |
| Deviation from DEER | DEER measures were modified as shown in the 5/2/13 ED Residential HVAC QM Disposition. |
| DEER Version | DEER14 |
| DEER Run ID and Measure Name (Sample) | Res-RefrigCharge-wtd |

Net to Gross

The NTG value was obtained from the “DEER2011_NTGR_2012-05-16.xls” on the DEER website as required by Version 5 of the California Public Utilities Commission (CPUC) Energy Efficiency Policy Manual [351]. The relevant NTGR for this measure is shown in Table 3 below.

Table 3 Net-to-Gross Ratio

| NTGR_ID* | Description* | Sector* | BldgType* | ProgDelivID | NTG* |
| --- | --- | --- | --- | --- | --- |
| Res-Default>2 | All other EEM with no evaluated NTGR; existing EEM with same delivery mechanism for more than 2 years | Res | Any | All | 0.55 |
| Res-sAll-mDuctSeal | Duct Sealing | Res | Any | PreReb | 0.78 |
| Res-sAll-mHVAC-RCA | HVAC Maintenance: Refrigerant Charge Adjustment (RCA) | Res | Any | PreReb | 0.78 |
| Res-Default-HTG-di | All other EEM with no evaluated NTGR; direct install hard-to-reach only. | Res | Any | DirInstall | 0.85 |

*Denotes that the column is taken from the DEER NTG Table.

Note that for the direct install delivery mechanism, a distinction between hard to reach and non-hard to reach markets will be made on a project by project basis. This work paper shows the NTG associated with a hard to reach direct install delivery mechanism and the defaulted NTG value, where in fact, a measure offered through direct install and is not “hard to reach” will receive a default NTG value.

Installation Rate

The installation rate (IR) is identified in the calculation attachment. This value is obtained from the support table available in READi. Currently there is no versioning on the installation rate table. To address appropriate selection of the installation rate the date of the workpaper will serve as the last date checked for updated IR values. The installation rate varies by end use, sector, technology, application, and delivery method. The relevant IR values for this measure are shown in Table 4 below.

The ED Disposition incorporates installation rates in its savings calculations. Specifically, they are 0.568 for duct sealing, 0.75 for RCA, and 1 for air flow adjustment and coil cleaning. A value of 0.45 is assumed for Design Capacity Sizing. Therefore no additional installation rate will be applied, and all GSIA values in this work paper are set to 1.

Table 4 Installation Rate

| GSIA_ID* | Description* | Sector* | BldgType* | ProgDelivID* | GSIAValue* |
| --- | --- | --- | --- | --- | --- |
| Def-GSIA | Default GSIA values | Any | Any | Any | 1 |

*Denotes that the column is taken from the DEER GSIA Table.

Incidence Rate

The incidence rate was relevant when the QM measures were offered as a package. Since the measures have been disaggregated, the incidence rate is set to 1.

Spillage Rate

Spillage rate will also be applied to measure however the values will not be tracked in the workpapers. The spillage rate will be tracked in an external table to be supplied to the Energy Division.

READi Technology Fields

To support the development of the ED ex ante tables, select fields from the ex ante database will be identified in the workpaper. For a full set of values associated with the measure in the workpaper refer the Excel calculation template.

Table 5 READi Tech IDs

| READi Field Name | Refrigerant Charge Adjustment | Condenser Coil Cleaning | Evaporator Coil Cleaning | Air Flow Adjustment | Duct Seal Med to Low | Duct Seal High to Low | Design Capacity Sizing |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Measure Case UseCategory | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC | HVAC |
| Measure Case UseSubCats | Space Heating and Cooling | Space Heating and Cooling | Space Heating and Cooling | Ventilation and Air Distribution | Ventilation and Air Distribution | Ventilation and Air Distribution | Space Heating and Cooling |
| Measure Case TechGroups | dX AC Equipment | dX AC Equipment | dX AC Equipment | HVAC Air Distribution | HVAC Air Distribution | HVAC Air Distribution | dX AC Equipment |
| Measure Case TechTypes | Split or Packaged DX AC Refrigerant System | Non-DEER | Non-DEER | Flow Control | Duct System Integrity - Residential | Duct System Integrity - Residential | SEER Rated Split System AC |
| Base Case TechGroups | dX AC Equipment | dX AC Equipment | dX AC Equipment | HVAC Air Distribution | HVAC Air Distribution | HVAC Air Distribution | dX AC Equipment |
| Base Case TechTypes | Split or Packaged DX AC Refrigerant System | Non-DEER | Non-DEER | Flow Control | Duct System Integrity - Residential | Duct System Integrity - Residential | SEER Rated Split System AC |

### 1.4.2 Codes and Standards Analysis

The measure contained in this work paper is generally not governed by either state or federal codes and standards.

However, in the event that ducts are found to be so badly damaged that some or all of the ductwork must be replaced, the total length of the replaced ducts shall be less than 40 linear feet in total per 2013 Title 24 Section 150.2(b) 1D, or the replaced ductwork must be installed and tested in accordance with the applicable requirements in 2013 Title 24 Section 150.2(b) 1D [355].

Title 24 does not deal with quality maintenance issues. The program requires the HVAC contractor to be license by the California State Licensing Board (CSLB) and the HVAC technicians to be EPA certified. Under state mechanical code, changes, alterations, or repairs of a minor nature not affecting structural features, egress, sanitation, safety, or accessibility as determined by the enforcing agency are exempt from the requirement to obtain a mechanical permit.

In the 2013 California Building Code [462], regarding Section 1.8.4 Permits, Fees, Applications, and Inspections, a written construction permit shall be obtained from the enforcing agency prior to the erection, construction, reconstruction, installation, relocation, or alteration of any mechanical system.

Exceptions:

- Work exempt from permits as specified in Chapter 1, Administration, Division II, Sections 112.2 through 112.2.3 of this code.

- Changes, alterations, or repairs of a minor nature not affecting structural features, egress, sanitation, safety, or accessibility as determined by the enforcing agency.

Table 6 Code Summary

| Code | Applicable Code Reference | Effective Dates |
| --- | --- | --- |
| Title 24 Part 6 (2013) | Section 150.2(b) 1D | July 1, 2014 |
| Title 24 Part 2 (2013) | Section 1.8.4 | January 1, 2014 |

### 1.4.3 Non-DEER Study Review

This work paper uses modified DEER savings, so no non-DEER studies were used in determination of the savings.

### 1.4.4  Measure and Base Case Effective Useful Life

In accordance with the Energy Division’s disposition [367], the Effective Useful Life (EUL) for HVAC Quality Maintenance is 5 years. Table 7 below identifies the value/methodology used for the measures in this work paper.

Table 7 DEER14 EUL Value/Methodology

| READi EUL ID | Market | Enduse | Measure | EUL (Years) | RUL (Years) |
| --- | --- | --- | --- | --- | --- |
| Non-DEER | Residential | HVAC | HVAC Quality Maintenance | 5 | N/A |

# Section 2. Energy Savings & Demand Reduction Calculations

Energy savings and demand reduction are based on the May 2, 2013 Energy Division Workpaper Disposition for Residential Quality Maintenance:

“2013_2014_ResHVACQMWorkpaperDisposition_2May2013.xlsx” (Attachment 2) [367]. For the following measures, newer DEER savings became available after the disposition was issued, so those more recent values were used instead: Res-RefrigCharge-wtd; Res-DuctSeal-HighToLow-wtd; and Res-DuctSeal-MedToLow-wtd.  Attachment 3 contains the revised calculations with DEER 2014 data.

The Design Capacity Sizing measure was not included in the Disposition or DEER 2014, so savings were estimated as a fraction of the total (lumped) energy and demand savings documented in the Disposition.  Expected Incidence Rate and Installation Rate values for this measure were conservatively estimated as 0.35 and 0.45 respectively with a calculated adjuster of: 0.35 * 0.45 = 0.1575. See Attachment 3 for all calculations.

Example for Single Family Home in climate zone 6:

If the sum of the RCA, Coil Cleaning, Air Flow, and Duct Sealing measures is 9.96 kWh, then the Design Capacity Sizing savings is: 0.1575 * 9.96 = 1.57 kWh.

All measures are anticipated to be updated in the near future using best available data and/or WO32 HVAC Impact Evaluation findings.

The remainder of Section 2 and Appendices A through D contain a description of the methods used to determine energy savings in the previous version of this work paper. Some of the measure information remains relevant to this work paper, but the resultant savings values are no longer applicable and are only kept here for historical documentation.

2.1 Packaged Treatment Approach

The deemed savings analysis used in this work paper uses DEER single family prototype file for DOE2 (eQUEST) batch runs.  Modifications were made to the input assumptions in the eQUEST simulation model to assess the impact of treatments for quality maintenance on an air conditioner unit.  The results from the batch runs were assembled to be used by the “Design of Experiments” [F], methodology to produce a “Regression Fit Model” to minimize the number of needed runs and maintaining statistical significance.  And lastly the results from the regression model were input into the “Expected Value Analysis” to come up with the estimated savings.

The eQUEST methodology for the motor retrofit measures utilizes the results from the “Design of Experiments” and “Expected Value Analysis” [J] QM measures, which separates the evaporator blower motor usage and run time hours.

### 2.1.1 Expected Value (EV) Analysis

The effect of each treatment on the energy use of a particular building depends on the as-found or existing conditions.  The effect of a measure consisting of a package of treatments is additionally influenced by treatment interactions.  Expected Value (EV) [J] analysis is used to take into account the variability of baseline conditions and treatment interactions to arrive at a final savings number for QM in each SCE climate zone.  The software package DPL7 [4] (Decision Programming Language) was used to perform calculations and generate graphics illustrating the inputs and results.

Refer to Appendix A for detailed descriptions of the Expected Values (EV) Analysis process.

### 2.1.2 Energy Simulation with eQUEST

eQUEST [9, G] is a DOE2 based simulation software package used to produce estimates of energy use of prototype residential building models.   DEER single family prototypes [12] were used as the basis for all eQUEST simulations.

To reach an overall measure energy savings, EV within a single climate zone using only eQUEST would require simulation runs for each treatment in each of the baselines as well as for each possible combination of treatments within the measure.  This quickly adds up to hundreds of runs even without considering multiple permutations of each treatment.  In order to reduce the number of runs and maintain a proper analysis of interaction complexity, a Design of Experiments process was used to specify a reduced number of runs that can be handled by using the batch process capability of eQUEST.  Once the runs were completed, the results were used to generate multi-variable regressions that can be used to calculate energy consumption independent of eQUEST.   These regressions are then used in an expected value analysis to generate a full range of expected baseline conditions and treatment outcomes along with associated probabilities.

Refer to Appendix B for detailed descriptions of the DOE2 eQUEST process.

### 2.1.3 Design of Experiment

Design of Experiments (DoEx) [F] is a branch of applied statistics that plans, conducts, and analyzes controlled tests to measure the effect that factors (such as efficiency, duct leakage, or cooling setpoint) have on a response (such as energy use). Using a DoEx approach allows evaluation of all factors and combinations of interactions that might affect a response while minimizing the number of needed runs and maintaining statistical significance.  To model all possible combinations of parameters for either the base case or QM case would require 112,500 simulation runs.  With DoEx this number was reduced to 68 runs needed for a statistically valid result when comparing to the results from running the eQUEST simulation.

Refer to Appendix C for detailed descriptions of the Design of Experiments (DoEx) process.

2.1.4 Savings Determination Steps

Since the quality maintenance measure consists of multiple treatments having interactive effects an analysis method that takes all of the treatment and interaction effects into account was required. The steps taken to achieve this are listed below:

- Estimation methods were developed that would allow simulation of the quality maintenance improvements.

- Seven factors that significantly impact energy usage in homes were selected for the purpose of building multivariate regressions to predict electric energy usage, electric peak demand, and gas energy usage for one and two story homes in each of the climate zones. Some of the factors also have the ability to be adjusted to accomplish the estimation methods developed in step 1.

- The highest and lowest likely values of each factor were determined as well as a midpoint value. A design of experiment approach was used to select 68 unique combinations of the seven factors for one and two story homes in each climate zone.

- Each of the seven factors was translated into eQUEST [G] inputs, and the 68 runs defined in step 2 were run using eQUEST’s batch processing capability for one and two story homes in each climate zone.

- The kWh, kW, and therm annual use results from the 68 runs were used to develop regressions.  Regression statistics were calculated to ensure the ability of the regressions to predict the responses.

- For each of the seven factors, probability distributions were developed for the range of values in the base case and after quality maintenance has been performed.

- The probability distributions of the seven factors were used in the regression equations to determine the probability distribution of kWh, kW, and therms in the base case and QM case for one and two story homes in each climate zone. The expected value (EV), or weighted average of the kWh, kW, and therms for the QM case was subtracted from the EV of the base case to determine the EV of the savings for one and two story homes in each climate zone.

- The EV savings calculated in step 8 were normalized by cooling capacity in tons. The one and two story savings for each climate zone were then weighted by the percentage of one and two story homes in the climate zone.

- Additional eQUEST runs were made with randomly generated values of the seven factors. The results of these runs were compared to the regression predictions using the same randomly generated values for the seven factors to test the ability of the regressions to predict energy usage for values of the seven factors that were not included in the 68 runs used to create the regressions.

Table 8 lists each of the possible treatments in the quality maintenance measure and a short description of the estimation method used to represent the effect of the treatment.

Table 8 Estimation Methods for QM Measure Treatments

| Treatment | Estimation Method |
| --- | --- |
| Refurbish Ducts | Airflow improvement, EER, and Cooling Capacity Improvement |
| Restore and Improve Duct Insulation | Duct heat transfer coefficient reduction (R-Value improvement) |
| Duct Seal | Duct leakage reduction |
| Clean Evaporator Coil and Blower | Airflow improvement and evaporator heat transfer improvement resulting in EER and cooling capacity improvement |
| New Air Filter to Match the Blower | Airflow improvement, EER improvement, and cooling capacity improvement |
| Clean Condenser Coil | Condenser heat transfer improvement resulting in Cooling Capacity improvement and EER improvement |
| Thermal Expansion Valve (TXV) Bulb Insulation and Attachment Correction or Replacement | EER and Cooling Capacity Improvement |
| Refrigerant Charge Correction | EER and Cooling Capacity Improvement |

Seven factors were selected that would significantly affect home energy usage, would adequately represent the possible range of homes in each climate zone and would allow for adjustment to represent the estimation methods in Table 9. Distributions of the possible values of each of the seven factors were then developed using various sources and methods.

Table 9 lists the factors and a short description of the source of each factor’s distribution of possible values. A more detailed description of the factors, the methods used for translation to eQUEST inputs to reflect the estimation methods in Table 9, and the development of the base case and quality maintenance case distributions for each factor can be found in Appendix A.

Table 9 Factors Affecting Energy Usage and Methods of Estimating Distribution of Factors

| Type | Unit | Method/Source for Estimating Distributions |
| --- | --- | --- |
| Refrigeration Impact Factor (RIF) | % energy impact | Robert Mowris data set [20] analysis. RIF is the factor representing the % energy impact resulting from airflow and refrigeration corrections in a sample of 56 residential units. RIF accounts for both airflow and refrigeration corrections and interaction effects between the two. |
| Duct Leakage | % of Airflow | Data set from Verified field studies [21], over 6,500 data points |
| Duct UA | Btu/(hr ° F) | DEER prototypes for area [3]; code and assumed levels of degradation for U-values |
| Tstat offset | ° F | RASS data transformed to 24 hr average setpoint [22] |
| Nominal SEER | Btu/(Watt-hr) | DEER values weighted by vintage [25] |
| AFUE | % Efficiency | Average Value provided by SCE from program data, assumed distribution |
| Shell UA | Btu/(hr ° F) | Wall/window/roof areas from prototype model; U-values from DEER [24] – change for each climate zone and vintage; includes infiltration |

Figure 1 shows the 7 input parameters and how they were expected to influence the calculated results. The green ovals are discrete chance nodes. Each node was assigned a range of values along with the probability of the occurrence of each value. The blue rectangles on the right hand side are value or result nodes.  The value node “Annual Result” performs calculations using the regression models for the climate zone to arrive at the expected value of total energy use for the residential single family prototype home. The blue result nodes simply represent the outputs that are generated for kW, kWh and therms.

Yellow boxes represent a decision; in this model the only decision is whether the base case or QM case is being evaluated. A final expected total annual energy use value is calculated for the base case and the QM case. The measure savings is the difference between them.

Refer to Appendix A for detailed descriptions of the Expected Values (EV) Analysis process.

Figure 1 Expected Value Analysis Influence Diagram

With the 7 factors defined, the next step was to determine the impact that the full range of those seven factors could have on energy consumption and demand. In order to represent the full range of possibilities a design of experiment approach was used to select combinations of the highest and lowest values for each factor that are likely to be encountered in the population of homes. By using the highest and lowest level of each factor the full possible effect of the factor is represented in the response.

Starting with DEER single family home prototypes developed in eQUEST, 68 runs with the selected combinations of high and low factors were run for both one and two story homes in each of the SCE climate zones.

Figure 2 below shows an example of the DEER single family prototypes that were used as to model the quality maintenance measure. Notice that the model contains two identical one story and two story homes that are rotated 90 degrees to capture the effect of orientation on the model.

Refer to Appendix B for detailed descriptions of the DOE2 eQUEST process.

Figure 2  eQUEST Single Family Home Prototype

The results of the 68 runs were then used to generate regression models that predict electric energy usage, peak electric demand, and gas energy usage. After the runs are made the responses kWh, kW, and therm were entered for each run and a regression was developed to predict each of the responses. Each regression is unique to a specific climate zone and to whether the home is one story or two stories. Further details of the regression models are included in Appendix C.

Figure 3: Example of Design of Experiment eQUEST Run Specification

Figure 4: Example Regression Equation

The regression above is a powerful tool that can predict energy usage based on the independent variables and the interaction effects for any combination of factors whose values are between the high and low values originally used in Design of Experiment.

Refer to Appendix C for detailed descriptions of the Design of Experiments (DoEx) process.

The expected value (EV) analysis was performed to determine deemed savings using the regression equations. EV analysis uses the entire distribution of possible values for each factor to generate a distribution of possible outcomes for each response based on the regression formula with the full range of possible factors and interaction effects considered.

Figure 5 below shows the base case and QM case distributions of energy usage (kWh) with a vertical line indicating the overall expected value, or weighted average kWh for the base case and QM case. The difference between the two overall expected values is the deemed savings. Both the base case and QM case distributions show the entire range of energy usage possible and the probabilities of each result given the distributions of the individual factors.

Figure 5: Energy Use Frequency Histogram for a Two Story House in Climate Zone 14 for Base Case and QM Case

## 2.2 Quality Assurance of Regression Equations

In order to determine how well the independent variables or factors predict the responses adjusted r2 was calculated for each of the regressions. Adjusted r2 is the proportion of variability in the runs used to generate the model that is accounted for by the regression, modified to adjust for the number of factors used in each regression so that it is not artificially inflated solely by the addition of more factors. Adjusted r2 has a maximum value of 1, which would indicate that all of the variability in the data used to generate a regression can be explained by the factors in the regression.  The coefficient of variation (CV) for each regression is the ratio of the error, represented by the standard deviation of the response, to the mean of the response, so a lower value indicates that more of the possible responses for a regression are grouped around the mean response. This test statistic allows us to compare the relative error or noise between all the regressions generated. Adjusted r2 and CV expressed as a percentage are shown in Table 10 for all of the regressions.

Table 10 Regression Statistics

|  | 1-Story Homes |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Adjusted R2 |  |  | CV% |  |  |
| CZ | Energy | Demand | Gas | Energy | Demand | Gas |
| 6 | 0.972224 | 0.971404 | 0.972373 | 1.464756 | 6.289007 | 1.148847 |
| 8 | 0.983416 | 0.96415 | 0.968547 | 0.198182 | 6.521897 | 1.140865 |
| 9 | 0.977354 | 0.966845 | 0.973745 | 2.993777 | 5.813375 | 1.186026 |
| 10 | 0.971275 | 0.969535 | 0.97959 | 3.472063 | 6.868524 | 1.290585 |
| 13 | 0.979742 | 0.973067 | 0.98313 | 3.034517 | 4.41989 | 1.056654 |
| 14 | 0.977796 | 0.978402 | 0.982771 | 3.568311 | 3.419301 | 1.137612 |
| 15 | 0.969776 | 0.985867 | 0.969168 | 4.877248 | 2.475972 | 1.027821 |
| 16 | 0.979221 | 0.970877 | 0.973757 | 2.120943 | 5.674676 | 1.557696 |
|  | 2-Story Homes |  |  |  |  |  |
|  | Adjusted R2 |  |  | CV% |  |  |
| CZ | Energy | Demand | Gas | Energy | Demand | Gas |
| 6 | 0.990281 | 0.970471 | 0.977382 | 1.37036 | 5.78782 | 1.696418 |
| 8 | 0.992164 | 0.9802 | 0.974789 | 0.174605 | 2.82 | 1.699357 |
| 9 | 0.989511 | 0.982957 | 0.980665 | 2.168868 | 2.449195 | 1.620275 |
| 10 | 0.988037 | 0.986151 | 0.980063 | 2.36131 | 2.316584 | 1.820752 |
| 13 | 0.979526 | 0.985784 | 0.987631 | 3.122054 | 2.006759 | 1.380155 |
| 14 | 0.987611 | 0.984591 | 0.982876 | 2.715626 | 1.885455 | 1.710556 |
| 15 | 0.983306 | 0.989676 | 0.972611 | 3.530875 | 1.472637 | 1.636588 |
| 16 | 0.987422 | 0.985767 | 0.976912 | 1.907418 | 2.224488 | 2.026474 |

In addition to calculating test statistics to determine how well the regressions describe the runs they were generated from, additional eQUEST modeling was performed with randomly selected values for each of the factors in climate zones 6 and 14. The results of these models were then compared with the regression responses when the same randomly selected values were input into the regressions for each climate zone. This test was performed to ensure the ability of the regressions to reasonably predict the responses with values that were not included in the runs used to generate the regressions. Bear in mind that these tests do not represent either the base case or quality maintenance case, as the values for the factors were randomly selected. The results of this regression check are presented graphically in Figures 6, 7 and 8 below. The Excel spreadsheet titled SCE Res Regression Check Calcs [29] shows details of the eQUEST simulation inputs and results.

Figure 6 Comparison of Regression Calculated Annual Energy Use to eQUEST Simulation Result

Figure 7 Comparison of Regression Calculated Annual Peak Demand to eQUEST Simulation Result

Figure 8 Comparison of Regression Calculated Annual Gas Use to eQUEST Simulation Result

## 2.3 Electric Energy Savings Estimation Methodologies, Normalization, and Weighting

The calculation of electric energy use for the Base case and the QM measure followed the methodology discussed in Section 2.0. The savings for the QM measure are estimated as follows.

QM Annual Electric Savings:

Energy Savings [kWh/Home] = EV of Base Case Annual Energy Use– EV of QM Annual Energy Use

Where:

EV = Expected Value

Annual Energy Use = Regressed annual kWh

In accordance with the Energy Division’s disposition [367], all UES values are revised as shown in Table 11.

Table 11 Revised HVAC Quality Maintenance Savings Values Per ED Disposition

| Original Work Paper Values (Single Family Home) |  |  |  | ED Disposition Values |  |  | Reduction Percentages |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CZ | kWh | kW | Therms | kWh | kW | Therms | kWh | kW | Therms |
| 6 | 36.0 | 0.320 | 4.63 | 18.1 | 0.020 | 1.13 | 50% | 94% | 76% |
| 8 | 57.6 | 0.478 | 4.72 | 31.0 | 0.064 | 1.15 | 46% | 87% | 76% |
| 9 | 137.6 | 0.657 | 5.47 | 37.8 | 0.054 | 1.25 | 73% | 92% | 77% |
| 10 | 140.8 | 0.979 | 5.74 | 35.9 | 0.069 | 1.42 | 74% | 93% | 75% |
| 13 | 184.6 | 0.707 | 8.78 | 54.1 | 0.070 | 2.03 | 71% | 90% | 77% |
| 14 | 203.0 | 1.587 | 6.64 | 70.0 | 0.092 | 1.90 | 66% | 94% | 71% |
| 15 | 319.2 | 0.934 | 1.47 | 83.9 | 0.072 | 0.61 | 74% | 92% | 59% |
| 16 | 118.7 | 0.797 | 15.15 | 23.9 | 0.064 | 4.94 | 80% | 92% | 67% |

| Original Work Paper Values (Multi Family Home) |  |  |  | ED Disposition Values |  |  | Reduction Percentages |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CZ | kWh | kW | Therms | kWh | kW | Therms | kWh | kW | Therms |
| 6 | 36.0 | 0.320 | 4.63 | 8.7 | 0.008 | 0.29 | 76% | 98% | 94% |
| 8 | 57.6 | 0.478 | 4.72 | 19.6 | 0.031 | 0.30 | 66% | 94% | 94% |
| 9 | 137.6 | 0.657 | 5.47 | 28.5 | 0.027 | 0.31 | 79% | 96% | 94% |
| 10 | 140.8 | 0.979 | 5.74 | 22.3 | 0.036 | 0.36 | 84% | 96% | 94% |
| 13 | 184.6 | 0.707 | 8.78 | 38.7 | 0.037 | 0.46 | 79% | 95% | 95% |
| 14 | 203.0 | 1.587 | 6.64 | 49.1 | 0.041 | 0.49 | 76% | 97% | 93% |
| 15 | 319.2 | 0.934 | 1.47 | 72.1 | 0.041 | 0.18 | 77% | 96% | 88% |
| 16 | 118.7 | 0.797 | 15.15 | 18.5 | 0.033 | 1.04 | 84% | 96% | 93% |

## 2.4 Demand Reduction Estimation Methodologies, Normalization, and Weighting

The calculation of electric demand for the base case and the measure cases followed the methodologies discussed in Section 2.0. However, the peak demand results from eQUEST do not conform to the DEER methodology for determining demand across a three-day peak heat wave. The following approach was employed to ensure the DEER methodology was applied to the TMY3 weather data.   The peak demand outputs from the eQUEST runs were input into DoEx to determine the demand regression. The regressed kW was then utilized in the EV analysis to estimate demand for the base case and the QM treatment case. The demand reduction for the QM measure is determined by EV is as follows:

QM Demand Reduction:

Demand Reduction [kW/Home= EV of Base Case Demand– EV of QM Demand]

Where:

EV = Expected Value

Demand = regressed annual peak-hour kW

These demand values were converted to represent the three-day heat wave peak demand via a “correction factor”. First, the three-day heat wave was located in the TMY3 weather file for each climate zone. The hourly demand from 2-5pm on these three, consecutive weekdays was averaged to provide demand across these 9 peak hours. These values were compared to the annual peak hour kW averaged across a selection of eQUEST runs from DoEx to determine the correction factor. Finally, this correction factor was applied to the EV demand results to approximate demand savings over the three-day 9-hour peak period.  The correction factors are shown in Table 12.

Table 12  Demand Adjustment Factors

| Climate Zone | TMY3 City | 1-story peak kW correction factor | 2-story peak kW correction factor |
| --- | --- | --- | --- |
| 6 | Los Angeles | 63.0% | 66.0% |
| 8 | Santa Ana - El Toro | 48.2% | 50.2% |
| 9 | Pasadena-Burbank | 91.8% | 94.0% |
| 10 | Riverside | 77.1% | 89.7% |
| 13 | Fresno | 94.4% | 95.7% |
| 14 | China Lake | 90.3% | 89.5% |
| 15 | Blythe-El Centro | 93.4% | 94.6% |
| 16 | Sandberg | 87.9% | 89.6% |

Electric demand reductions per home were determined for both the one and two story homes in each climate zone and were then normalized to the cooling capacity in tons of the weighted average one and two story homes for each zone. The one and two story reductions were then weighted by the percentages of one and two story homes in the climate zone to obtain a single deemed demand reduction value for each climate zone and measure in units of kW/ton.

In accordance with the Energy Division’s disposition [367], all UES values are revised as shown in Table 11 and 12.

## 2.5 Gas Energy Savings Estimation Methodologies, Normalization, and Weighting

The calculation of gas energy use for the base cases and the measure cases for each measure followed the methodologies discussed in Section 2.0. Savings was then estimated as the difference in gas energy use between the base case and measure case. The savings for the QM measure are estimated as follows.

Annual Gas Savings:

Energy Savings [therms/Home] = EV of Annual Base Gas Usage – EV of QM Annual Gas Usage

Where:

EV = Expected Value

Gas Usage = regressed annual therms

Gas savings per home were determined for both the one and two story homes in each climate zone and were then normalized to the cooling capacity in tons of the weighted average one and two story homes for each zone. The one and two story savings were then weighted by the percentages of one and two story homes in the climate zone to obtain a single deemed savings value for each climate zone and measure in units of therms/ton.

In accordance with the Energy Division’s disposition [367], all UES values are revised as shown in Table 11.

# Section 3. Load Shapes

The difference between the base case load shape and the measure load shape would be the most appropriate load shape; however, only end-use profiles are available.  Therefore, the closest load shape chosen for this measure is the DEER:HVAC_Eff_AC load shape.  See Table 13 for a list of all Building Types and Load Shapes.  See the KEMA report [31] for a more thorough discussion regarding the load shapes for this measure.

Table 13 Building Types and Load Shapes

| Building Type | E3 Alt. Building Type | Load Shape |
| --- | --- | --- |
| Residential Single Family | RES | DEER:HVAC_Eff_AC |
| Residential Multi-Family | RES | DEER:HVAC_Eff_AC |
| Residential Mobile Home - Double-Wide | RES | DEER:HVAC_Eff_AC |

# Section 4. Base Case & Measure Costs

## 4.1 Base Case Cost

The base case is the customer’s existing equipment; therefore the base case cost is $0.

## 4.2 Measure Case Cost

### Measure costs are first calculated per household and then divided by a climate-specific tonnage to determine per-ton costs.

### 4.2a Refrigerant Charge Adjustment

DEER 2008 [215] provides per-ton costs for the following:

- Increase Refrigerant Charge - Typical (< 20% rated charge)

- Increase Refrigerant Charge - High (>= 20% rated charge)

- Decrease Refrigerant Charge - Typical (< 20% rated charge)

- Decrease Refrigerant Charge - High (>= 20% rated charge)

These costs are weighted based on PG&E’s 2010 RCA participant data [13] and multiplied by 3.27 tons/household to come up with single per-ton costs of $34.86 for material and $120.46 for labor; it is assumed that this distribution is typical for California.

Table 14 2010 PG&E RCA Program distribution on percentage charge

| 2010 PG&E RCA program distribution |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| RCA Percent Charge | Distribution Count | Category | Percentage of Total | DEER 2008 Cost Case | Material Cost | Labor Cost |
| 150.00% | 16 | >=20% Over | 2.05% | Decrease Refrigerant Charge - High (>= 20% rated charge) | $10.04 | $36.82 |
| 140.00% | 177 |  |  |  |  |  |
| 120.00% | 8 |  |  |  |  |  |
| 119.99% | 628 | <20% Over | 29.47% | Decrease Refrigerant Charge - Typical (< 20% rated charge) | $5.58 | $36.82 |
| 110.00% | 2257 |  |  |  |  |  |
| 100.10% | 0 | N/A | N/A | N/A |  |  |
| 100.00% | 221 | <20% Under | 57.76% | Increase Refrigerant Charge - Typical (< 20% rated charge) | $11.55 | $36.82 |
| 99.90% | 3218 |  |  |  |  |  |
| 90.00% | 2127 |  |  |  |  |  |
| 80.99% | 88 |  |  |  |  |  |
| 80.00% | 880 | >=20% Under | 10.72% | Increase Refrigerant Charge - High (>= 20% rated charge) | $19.93 | $36.82 |
| 60.00% | 84 |  |  |  |  |  |
| 50.00% | 34 |  |  |  |  |  |
| 40.00% | 51 |  |  |  |  |  |

### 4.2b Duct Sealing

DEER 2008 provides identical per-household costs for the following:

- Duct Sealing (Total Leakage Reduced from 24% of AHU flow to 12%)

- Duct Sealing (Total Leakage Reduced from 40% of AHU flow to 12%)

Since the QM program will not perform diagnostic testing on the customer’s duct system, only duct sealing will be completed by participating contractors/technicians. Mike Yim [14] of Summit Blue Consulting estimated one hour of labor for the duct diagnostic testing. The DEER cost is based on 6 man hours, so 1 hour is subtracted out to yield $46.46 for material and $368.23 for labor.

### 4.2c Condenser and Evaporator Coil Cleaning

The DEER 2008 per-household cost for cleaning condenser coils is $0.00 for material and $114.15 for labor. It is assumed that the cost is the same for cleaning condenser and evaporator coils.

### 4.2d Air Flow Adjustment

It is assumed that the per-household cost for an air flow adjustment is the labor cost of an air balance on a package rooftop AC unit, which is $415.00 from RS Means 2010 Building Construction Data [463].

### 4.2e Design Capacity Sizing

It is assumed that the per-household cost for design capacity sizing is the labor cost involved with performing a residential load calculation (e.g. Manual J). Using the DEER default labor rate of $67.88 and an estimated 4 hours for the calculations, the cost is $271.52.

### 4.2f Cost Permutation by Climate Zone

The per-household costs are divided by climate-specific average tonnages from DEER to determine individual costs per climate zone. The following is an example for refrigerant charge adjustment:

Table 15 Refrigerant Charge Adjusment Costs

| CZ | Tons | Material Cost Per Household | Labor Cost Per Household | Material Cost Per Ton | Labor Cost Per Ton | Full Cost, GMC Per Ton |
| --- | --- | --- | --- | --- | --- | --- |
| 6 | 3.35 | $22.66 | $78.30 | $6.76 | $23.37 | $30.14 |
| 8 | 3.12 | $22.66 | $78.30 | $7.26 | $25.10 | $32.36 |
| 9 | 3.48 | $22.66 | $78.30 | $6.51 | $22.50 | $29.01 |
| 10 | 3.59 | $22.66 | $78.30 | $6.31 | $21.81 | $28.12 |
| 13 | 3.33 | $22.66 | $78.30 | $6.80 | $23.51 | $30.32 |
| 14 | 4.24 | $22.66 | $78.30 | $5.34 | $18.47 | $23.81 |
| 15 | 4.62 | $22.66 | $78.30 | $4.90 | $16.95 | $21.85 |
| 16 | 3.3 | $22.66 | $78.30 | $6.87 | $23.73 | $30.59 |

All cost calculations are in Attachment 4.

## 4.3 Gross and Incremental Measure Cost

### 4.3.1 Gross Measure Cost

For REA measures, the Gross Measure Cost (GMC) is the full measure cost as shown in Table 15.

For the ROB measure (Design Capacity Sizing), the GMC is also the full measure cost because the incremental cost between a right-sized system and a 20% oversized system only consists of the sizing calculation performed by the contractor. The per-ton material and labor costs between the 2 systems are assumed to be the same.

### 4.3.2 Incremental Measure Cost

For REA measures, the Incremental Measure Cost (IMC) is the same as the GMC.

For the ROB measure, the IMC is the same as the GMC due to the reason presented in Section 4.3.1.

# Attachments

# References

[31]

[215]

[351]

[355]

[367]

[462]

[463]

1. ACCA, “Maintenance of Residential HVAC Systems” - ANSI/ACCA Standard 4, 2008. https://www.acca.org/industry/ansi-standards

2. Itron, Inc. “2008 Database for Energy Efficiency Resources”, Version 2008.2.05, December 2008. http://www.deeresources.com/

3. Database for Energy Efficiency Resources (DEER) Single Family Prototype Input File. http://www.doe2.com/download/DEER/MAStool/

4. DPL – Decision Programming Language, Release 7.00.20, Copyright 2003-2010 by Syncopation software, Inc http://www.syncopation.com/?gclid=CJXd6Nfp1qoCFVMZQgodwHBO7w

5. Robert Mowris & Associates, Anne Blankenship, and Ean Jones. “Field Measurements of Air Conditioners With and Without TXVs”, paper for 2004 ACEE Summer Study Proceedings, 2004.

6. 2008 Building Energy Efficiency Standards for Residential and Nonresidential Buildings, SCE ref. 208.

7. Itron, Inc. “DEER NTG Values – 16 February 2009 Supplemental 2009-2011 Application Filings – Updated DEER NTGR Values – 053008.spreadsheet”, October 2008. http://deeresources.com/index.php?option=com_content&view=article&id=65&Itemid=57

8. Itron, Inc. “DEER EUL/RUL (Effective/Remaining Useful Life) Values, Updated 10 October 2008. http://www.deeresources.com/

9. eQUEST – Building Energy Use and Cost Analysis Software, developed by James J. Hirsch & Associates (JJH), version 3.64 was the latest release. http://www.doe2.com/

10. Energy Savings and EUL results for Quality Maintenance Measures, June 2011.

See SCE_QM_Savings at top of page.

11. DEER Single Family Prototypes with adjusted inputs.  Adapted from 2004-2005 Database for Energy Efficiency Resources (DEER) Update Study, Final Report, prepared for Southern California Edison by Itron, Inc. with support from J. J. Hirsch and Associates, December 2005.

12. Measure Costs Analysis spreadsheet, January, 2012.

13. Mike Yim, Summit Blue Consulting, e-mail message on duct seal cost, July 25, 2011.

14. California Statewide Residential Appliance Saturation Study, http://websafe.kemainc.com/RASS2009/Default.aspx

15. Mowris personal communication via e-mail, May 11, 2011 at 1:37PM.

16. Mowris’ dataset of field measurements for 56 residential units 2004 and derivation of RIF,

17. MDSS_PGE_duct leak_Distribution_Analysis, June 2011

18. Tstat probability_v4, June 2011

19.  California Title 24 thermostat schedule for Residential, “2005 Residential ACM Manual.”

20. DEER SFRes Properties- Capacity-SEER, November2011

21. Vintage Distribution of Home Type, November 2011

22. Peng Xu, Joe Huang, Norman Miller, Nicole Schegel. “Effects Of Global Climate Changes On Building Energy Consumption and Its Implications on Building Energy Codes and Policy in California”, PIER Project Report.  September 2009.

23. Design Expert version 8.0.5 Stat Ease, Inc. 2021 East Hennepin Ave., Suite 480, Minneapolis, MN 55413. http://www.statease.com/dx8descr.html

24. Regressions, June 2011

25. Regression Check Results, June 2011

26. Architectural Energy Consultants (AEC). “2005 Residential ACM Manual.” CEC-400-2005-005-CMF. 2005http://www.energy.ca.gov/title24/2005standards/residential_acm/2005_RES_ACM_CHAPT4.PDF

27. California Energy Commission (CEC). “Nonresidential Alternative Calculation Method (ACM) Approval Manual.” CEC-400-2008-003-CMF. Section 2.5.2.10, Page 2-74. December 2008. http://www.energy.ca.gov/title24/2008standards/

28. Pigg, Scott, Central Air Conditioning in Wisconsin: A Compilation of Recent Field Research, ECW Report Number 241-1, May 2008.

29. Results are summarized in “Table 14 – Mean System Airflow…” of the PIER report Efficiency Characteristics and Opportunities for New California Homes by Proctor, Chitwood and Wilcox for the CEC.

30. KEMA, The Cadmus Group, and Summit Blue Consulting. “Evaluation Measurement and Verification of the California Public Utilities Commission HVAC High Impact Measures and Specialized Commercial Contract Group Programs.” CPUC. February 10, 2010.   http://www.cpuc.ca.gov/PUC/energy/Energy+Efficiency/EM+and+V/

31. Savings and weightings for EUL, December 2011.

32. Itron Inc.  2004-2005 Database for Energy Efficiency Resources (DEER) Update Study - Final Report -- Dec. 2005.  SCE Ref 26.

33. SCE Emails regarding SEER AFUE

34. Workpaper disposition for residential HVAC Quality Maintenance California Public Utilities Commission, Energy Division, May 2, 2013

# Glossary of Terms and Acronyms

The following definitions are used throughout this work paper.

- ANSI/AHRI Standard 210/240-2008 – The purpose of this standard is to establish, for Unitary Air-Conditioners and Air-Source Unitary Heat Pumps: definitions, classifications, test requirements, rating requirements, minimum data requirements for published ratings, operating requirements, marking and nameplate, and conformance conditions.  This standard is intended for the guidance of the industry, including manufacturers, engineers, installers, contractors, and users.

- Air Conditioning Contractors of America, Standard 4 (ACCA 4) – The ANSI/ACCA Standard 4 Maintenance of Residential HVAC Systems-2008.  The purpose of this standard is to establish minimum inspection requirements in the maintenance of HVAC equipment found in one-family and two-family dwellings of three stories or less.

- Base case cost - The cost for base case equipment/treatment per common unit.

- CPUC Energy Division (ED) - The California Public Utilities Commission (CPUC) regulates privately owned electric communications, electric, natural gas, water, railroad, rail transit, and passenger transportation companies.  The CPUC's Energy Division develops and administers energy policy and programs “to serve the public interest”, advise the Commission, and ensure compliance with the Commission decisions and statutory mandates.

- Decision Programming Language (DPL) – The software package DPL is a decision support software tool used to perform calculations and generate graphics illustrating the inputs and results.  http://www.syncopation.com/?gclid=CJXd6Nfp1qoCFVMZQgodwHBO7w

- Design of Experiments (DoEx) – A software tool used for statistical process, resulting in a statistically valid regression model which accounts for the full range of treatment interactions for this quality maintenance work paper.  See Appendix C for statistical process.

http://www.statease.com/dx8descr.html

- eQUEST (DOE2) – Software to perform detailed comparative analysis of building designs and technologies by applying sophisticated building energy use simulation techniques. SCE requires that eQUEST version 3.64 or newer shall be used for this work.

http://doe2.com/eQUEST/

- Databases for Energy Efficient Resources (DEER) - The DEER provides estimates of the energy-savings potential for a variety of technologies of measures in residential and nonresidential applications.  http://www.deeresources.com/

- DEER Single Family Prototype - The DEER Single Family Prototype describes a single site configuration, including one or multiple building shells served by one or more HVAC system types.  Prototype characteristics correspond to eQUEST building “creation wizard” inputs, where the characteristics were developed specifically for DEER analysis.    http://www.doe2.com/download/DEER/MAStool/

- Expected Value Analysis (EV) – Using the DPL software, the measure package value is determined by probability based analysis to make an expert projection of what the likely states for parameters might be with a reasonable estimation of their probability.  The “expected value” is a weighted value based on multiple parameters.

- HVAC - The heating, ventilation and air conditioning system(s) in a home used for heating, cooling, and maintaining the home at a controlled temperature, surrounded by fresh air, at a humidity level that is safe and comfortable for the building and its contents.

- Incremental Measure Cost (IMC) - The value of the incremental cost of the measure (measure equipment cost less base equipment cost) per common unit.

- Labor cost – The cost of labor to perform the work of specific measures/treatments.

- Measure Case Cost – The cost for measure case equipment/treatment per common unit.

- SCE– Southern California Edison utility company.

- Implementer - A QM Implementer is a company that provides documented verification of work performed by licensed HVAC contractors performing a specified type of work or service. In the context of the Program, the service which the QM Implementer is to follow a program performance specification, market, recruit, and train licensed HVAC contractors and their technicians to offer the comprehensive quality maintenance service to the customers.

- Regression Fit Model – Regression is a term for all methods that fit a mathematical model to observed data in order to quantify the relationship between independent and dependent variables.  The fitted model is then used to describe the relationship between the two groups of variables and to predict new values of the dependent variable.

- Quality Maintenance (QM) – ACCA Standard 4 defines what must be done to implement Quality Maintenance on residential HVAC systems.  Using multiple treatments/measures the HVAC system and its elements are maintained on a regular interval to provide the intended thermal comfort and energy efficiency.

- Work Paper (WP) - A document developed by the utility that documents the product description, savings methodology, measure costs, effective useful life, and net-to-gross ratios.

# Appendix A Expected Values (EV) analysis

## Expected Values (EV) Analysis Process

The first step in the EV process was to identify the relevant factors that impact the same end-uses that the treatments will impact.  As shown in Table A1, there are seven factors identified which significantly affect home HVAC energy use.  The factors for refrigeration and airflow, ductwork insulation, and ductwork leakage have values and probabilities assigned to simulate the effect of the treatments.  The factors for nominal SEER, furnace AFUE, thermostat setting and shell UA are assigned values and probabilities to represent the variation across the population of residential single family and duplex dwellings.  The influence diagram is resolved into a decision tree, Figure A1, to show how a range of state assignments are made for each factor, with each state assigned a probability and a value that cascades through to the final result.  The policy tree represents 225,000 iterations leading to the final values. Each factor is described below along with the methodology for assigning the range of values and probabilities.

Figure A1: Expected Value Decision Tree

Table A1 below is a summary of the seven factors and the sources used in the Expected Value Analysis

Table A1 Factors Used in Expected Value Analysis

| Factor Number | Type | Unit | Source |
| --- | --- | --- | --- |
| 1 | Refrigeration Impact Factor (RIF) | % energy impact | Robert Mowris data set analysis5. Results included refrigerant charge as well as other services. |
| 2 | Duct Leakage | % | PG&E data set from field studies, over 6,500 data points |
| 3 | Duct UA | Btu/(hr °F) | DEER prototypes for area; code and assumed levels of degradation for U-values |
| 4 | Tstat offset | °F | RASS18 data transformed to 24 hr average setpoint |
| 5 | Nominal SEER | Btu/(Watt-hr) | DEER values weighted in each climate zone by vintage. |
| 6 | AFUE | % efficiency | Informed engineering estimate |
| 7 | Shell UA | Btu/(hr °F) | Wall/window/roof areas from prototype model; U-values from DEER – change for each climate zone and vintage; includes infiltration |

## Regression Factors, eQuest Input Translation, and Distribution Development

This section of the work paper details how each of the 7 factors used in the regressions were translated to eQUEST inputs and how the distributions representing the base cases and QM cases were developed.

- Refrigeration Impact Factor (RIF)

RIF is the factor created to represent improvements in refrigeration efficiency and airflow from the implementation of the refrigeration and airflow treatments. These include: duct refurbishment, evaporator and blower cleaning, air filter replacement, condenser coil cleaning, TXV maintenance or replacement, and refrigerant charge correction [5,19]. While it is possible to assign a separate efficiency improvement to each treatment, there is currently no solid basis for how to adjust for interactivity between treatments.

The refrigeration impact factor is calculated as:

RIF =1 - (% overall energy impact)

A unit that is ideally charged with adequate airflow would have zero energy impact and a RIF = 1.

RIF is represented in eQUEST using four inputs (KEYWORDS):

Supply air flow – (SUPPLY-FLOW)

Total Cooling capacity – (COOLING-CAPACITY)

Sensible cooling capacity – (COOL-SH-CAP)

Compressor power – (COOLING-EIR)

Field data from a study performed by Mowris [5] was used to derive RIF and the impact of a given RIF on each of the four eQUEST inputs above. The advantages of this data set are that it is the best available published source, and more importantly, the results are based on the implementation of the same set of service measures. This means that the interactive effects of the refrigeration and airflow related treatments are already reflected in the measured results.

The Excel spreadsheet titled RIF [20] contains Mowris’ dataset of field measurements for 56 residential units. The results are grouped into bins based on the "% overall energy impact", column AF in Tab DEER-RCA Data. Based on feedback from the Energy Division of the CPUC during a May 10, 2011 meeting, the data were further separated into high and low refrigerant charge groups as shown in Table A2.

Table A2 Mowris Data Distribution

Recall that the design of experiment requires a high value and a low value for each factor to capture the range of possible values as well as a midpoint factor to test for curvature in the regression. For RIF, site 15 was selected to represent the high RIF, and a RIF of 1.0 having no impact on the unit’s efficiency was chosen to represent the low RIF. Site 49 was chosen to represent the midpoint for RIF. By using a single site to represent the high and midpoint values eQUEST inputs could be generated that were based directly on the data resulting in each RIF. Table A3 below shows the adjustments applied for each of the eQUEST inputs to model the high, low, and midpoint RIF factors.

Table A3 RIF impacts and assumptions for calculating eQUEST Inputs for DoEx Runs

| Site | RIF, Refrig Impact Factor | % overall energy impact | Cooling-eir base fraction | Cooling-Capacity base fraction | Cool-sh-cap base fraction | Typical CFM_ton | External SP |
| --- | --- | --- | --- | --- | --- | --- | --- |
| XX | 1.00 | 0% | 1.000 | 1.000 | 1.000 | 400 | 0.50 |
| 49 | 1.087 | -8.68% | 1.0972 | 0.8843 | 0.8745 | 350 | 1.00 |
| 15 | 1.269 | -26.93% | 1.3984 | 0.8964 | 0.9414 | 225 | 2.00 |

To determine the distribution of RIF for the base case the Mowris data was grouped into 6 bins ranging from no energy impact to 25.7% energy impact due to refrigerant charge level and airflow. The number of sites in each bin was divided by the total number of sites to determine the base case probability for each bin. To arrive at the distribution for the QM case it was assumed that in the top 4 bins all but 10% of the sites within the bin achieve a RIF of 1.0 and all but 30% in the next lowest bin achieve a RIF equal to 1.0. Table A4 below shows the 6 bins and the probability distributions used for the base case and QM case.

Table A4 RIF Values and Probabilities

| Bin | Average energy impact | # | Base Prob. | QM Prob. | RIF (1-%impact) | Cooling-eir base fraction | Cooling-Capacity base fraction | Cool-sh-cap base fraction | CFM / ton |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Large Impact | -25.70% | 6 | 0.1071 | 0.0107 | 1.257 | 1.40 | 0.90 | 0.94 | 225 |
|  | -15.04% | 16 | 0.2857 | 0.0286 | 1.150 |  |  |  |  |
| Moderate Impact | -8.75% | 14 | 0.2500 | 0.0250 | 1.087 | 1.10 | 0.88 | 0.87 | 350 |
|  | -5.13% | 12 | 0.2143 | 0.0214 | 1.051 |  |  |  |  |
|  | -1.45% | 8 | 0.1429 | 0.0429 | 1.015 |  |  |  |  |
| High Efficiency | 0% | 0 | 0.0000 | 0.8714 | 1.000 | 1.00 | 1.00 | 1.00 | 400 |
|  | Total | 56 | 1 | 1 |  |  |  |  |  |

- Ductwork Leakage

Ductwork leakage occurs in both the supply and return ducts.  Leaks can be to the outside or to the inside of the building shell.  If air is leaked to the outside (in the attic) then the space becomes either pressurized or depressurized.  The difference between the volume of air delivered to the space and the volume removed is made up by increased house infiltration or exfiltration as shown in Figure A2.

FigureA2. Duct Loss and Gain Components in DOE2.2

The assumed ranges of total air leakage and the associated probability of occurrence are shown in Table A5. The simulation of duct leakage was performed in accordance with the 2005 DEER Report. [26] It assumes that a percentage of the supply leakage goes into the unconditioned attic with the remainder leaking to the conditioned spaces. The probability distribution is based on a dataset of field measurements from a California duct test and seal program.  The data was divided into bins with the average value shown in Table A5. The complete dataset is included in the attached Excel spreadsheet titled, Duct_Leak_Distribution_Analysis.[21]

Table A5 Duct Leakage Values and Probabilities

|  | EV Factor for Duct Leakage | Base Probability | QM Probability |
| --- | --- | --- | --- |
| Super Leaky | 40.00% | 36.60% | 3.7% |
|  | 24.00% | 28.24% | 10.1% |
| Leaky | 19.00% | 24.57% | 19.1% |
|  | 12.00% | 10.45% | 19.7% |
| OK | 8.50% | 0.14% | 47.4% |

- Ductwork Insulation

This treatment installs new duct insulation or repairs existing insulation to achieve an increase in overall R-value. Because there were no available datasets or studies to draw from, a series of assumptions were made to define this factor for the design of experiment runs used to generate the regressions. The Duct UA factor represents the combined UA of the supply and return ducts. The UA is the overall heat loss coefficient of the duct based on the R-values of the insulation, air film and duct material multiplied times the external duct area. For this analysis the R-value is assumed to change between the base case and the QM case while the duct area is kept constant for the one and two story homes across all vintages. The area does change according to vintage in the DEER prototypes since the DEER calculated value is tied to conditioned floor area, however this difference is relatively small and could be compensated for in the probability distribution.

Although a single factor for UA is used for the regression, the inputs that are used in eQUEST will treat supply duct UA and return duct UA separately since the temperature differential in the supply duct is much greater than in the return duct. However, because the assumed proportion of return duct area to supply duct area is constant, the combined value is a valid parameter for the regression analysis.

The probability distributions for the base case and the QM measure case are shown in Table A6. The distribution shifts toward a higher average R-value of duct insulation. These values are best characterized as an informed estimate and should be revised as data becomes available.

Table A6 Probability Values for Duct UA

| Equivalent R-Value | 1-story Duct UA, Btu/ft²·°F·h | 2-story Duct UA, Btu/ft²·°F·h | Base Probability | QM Probability |
| --- | --- | --- | --- | --- |
| 2.8 | 139 | 239 | 15.0% | 2.5% |
|  | 110 | 189 | 20.0% | 13.9% |
| 5.8 | 81 | 139 | 40.0% | 35.9% |
|  | 65 | 112 | 15.0% | 30.9% |
| 8.7 | 50 | 86 | 10.0% | 16.8% |

- Thermostat Setting

Thermostat settings are an important factor in determining energy savings. In order to represent the diversity of use, a range of values was established which encompasses both the energy conscious households and those that are heavy users of air conditioning and heating. The standard Title 24 thermostat schedule as found in the Residential Alternative Calculation Method Manual [23.30] was chosen as the mid-range point. This schedule is also the default thermostat schedule in the DEER prototypes. At one extreme is the ‘Saver’ schedule with an 82 °F constant cooling setpoint and at the other extreme is the ‘Comfort’ schedule with a 75°F constant cooling setpoint. The thermostat setting factor for generating regressions is expressed only in terms of cooling, however heating setpoints are taken into account as well. The three schedules including heating and cooling setpoints are shown in TableA7. These are the schedules that were used in the eQUEST runs to generate the results used in Design of Experiment to create the regression models. The 24-hour average of the Title 24 schedule is used as the reference point to calculate a thermostat setting factor defined as:

Tstat Offset = (24 hr average of cooling setpoints) - 79.7

Table A7 Schedules Used for eQUEST Simulations

|  | Title 24 |  | Saver |  | Comfort |  |
| --- | --- | --- | --- | --- | --- | --- |
| Hour | Heating Setpoint | Cooling Setpoint | Heating Setpoint | Cooling Setpoint | Heating Setpoint | Cooling Setpoint |
| 1 | 65 | 78 | 65 | 82 | 71 | 75 |
| 2 | 65 | 78 | 65 | 82 | 71 | 75 |
| 3 | 65 | 78 | 65 | 82 | 71 | 75 |
| 4 | 65 | 78 | 65 | 82 | 71 | 75 |
| 5 | 65 | 78 | 65 | 82 | 71 | 75 |
| 6 | 65 | 78 | 65 | 82 | 71 | 75 |
| 7 | 65 | 78 | 65 | 82 | 71 | 75 |
| 8 | 68 | 83 | 65 | 82 | 71 | 75 |
| 9 | 68 | 83 | 65 | 82 | 71 | 75 |
| 10 | 68 | 83 | 65 | 82 | 71 | 75 |
| 11 | 68 | 83 | 65 | 82 | 71 | 75 |
| 12 | 68 | 83 | 65 | 82 | 71 | 75 |
| 13 | 68 | 83 | 65 | 82 | 71 | 75 |
| 14 | 68 | 82 | 65 | 82 | 71 | 75 |
| 15 | 68 | 81 | 65 | 82 | 71 | 75 |
| 16 | 68 | 80 | 65 | 82 | 71 | 75 |
| 17 | 68 | 79 | 65 | 82 | 71 | 75 |
| 18 | 68 | 78 | 65 | 82 | 71 | 75 |
| 19 | 68 | 78 | 65 | 82 | 71 | 75 |
| 20 | 68 | 78 | 65 | 82 | 71 | 75 |
| 21 | 68 | 78 | 65 | 82 | 71 | 75 |
| 22 | 68 | 78 | 65 | 82 | 71 | 75 |
| 23 | 68 | 78 | 65 | 82 | 71 | 75 |
| 24 | 65 | 78 | 65 | 82 | 71 | 75 |
| 24 hour average |  | 79.7 |  | 82 |  | 75 |
| cooling setpoint |  |  |  |  |  |  |
| Tstat Offset |  | 0 |  | 2.3 |  | -4.7 |

The Tstat Offset and associated probabilities used in the Expected Value analysis are shown in Table A8. The Excel workbook titled Tstat_probability_v4 [22], contains the derivation of the thermostat offset value probability. The RASS database was queried to get survey results of reported cooling thermostat setpoints during the morning, day, evening, and night for single family homes in all of California. The "evening" time block was selected as being the most probable indication of the daily pattern for those homes that would be targeted for a QM program. The OFF category response was eliminated since they would probably have the lowest usage and would be unlikely to participate in a QM program. Since the survey results are not coordinated between time blocks the data were statistically distributed into five daily schedules. This resulted in the five value range of Tstat Offset shown in the table.

Table A8 Tstat Offset Values and Probability

| 24 hour Average | Tstat Offset | Tstat Probability |
| --- | --- | --- |
| 82.00 | 2.30 | 0.172 |
| 81.00 | 1.30 | 0.045 |
| 78.75 | -0.95 | 0.32 |
| 76.30 | -3.53 | 0.273 |
| 75.00 | -4.70 | 0.19 |
| Tstat Offset = 78.03 (24 hr weighted avg) |  |  |

- Nominal SEER

To generate the regressions a SEER of 15 was chosen for the upper limiting case and a SEER of 7 was chosen for the lower limiting case. A SEER of 11 was chosen for the 4 midpoint runs. Nominal SEER is converted to the eQUEST input EIR or electric input ratio, which is the ratio of electric energy used to cooling energy provided. SEER includes the power used for the supply and condenser fans in addition to the compressor power. Since the supply and condenser fans were modeled separately their power was removed from the EIR term. The following equation was derived from Figure 5, Performance Characteristics of SEER-rated Cooling Systems” from EER & SEER as Predictors of Seasonal Cooling Performance by James J. Hirsch and Associates, December 15, 2003.

EER = 2.08 + 0.73 * SEER

The EER is then converted to EIR for input to eQUEST. SEER and EER are based on total electric power where EER is Cooling capacity (Btu/hr) divided by total electrical power in Watts. The eQUEST model has the blower and the condenser fan entered as separate items so the power for those two motors must be removed to get the proper EIRc based on compressor power only.

EER 	= Capacity / Total Power

Total Power = EER / Capacity = Comp + Blower + Condenser

Comp = (EER / Capacity) – Blower - Condenser

EIRc = Comp * 3.413 / Capacity

Where EIRc + EIR of the compressor only

EIRc = ((EER / Capacity) – Blower – Condenser) * 3.413 / Capacity

The EIRc is then modified by the RIF to get the final EIR value that is entered into eQUEST.

The values used for the distribution of Nominal SEER in single family homes were derived from the DEER Residential Lookup Table and the RASS survey [18]. The data summary showing how the distribution to value bins was made is contained in the Excel spreadsheet titled DEER SFRes- Properties- Capacity-SEER. [24] Table A9 shows the average bin values and associated probabilities for each climate zone.  Even though the SEER values did not change, the probabilities for the pre-2005 vintages were used to fit into the format of the expected value calculation.

The nominal SEER does not change from the base case to the QM case, rather RIF changes, which in turn affects the actual SEER.

Table A9 Probability of Nominal SEER Weighted by Vintage in SCE Climate Zones

|  |  | California Climate Zones |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Vintage | SEER | CZ_06 | CZ_08 | CZ_09 | CZ_10 | CZ_13 | CZ_14 | CZ_15 | CZ_16 |
| <1978 | 10 | 0.703726 | 0.713641 | 0.742695 | 0.333565 | 0.417798 | 0.334374 | 0.313508 | 0.622762 |
| 78-92 | 10 | 0.173839 | 0.169203 | 0.164058 | 0.356691 | 0.281689 | 0.406349 | 0.385711 | 0.245739 |
| 93-01 | 10 | 0.068547 | 0.060026 | 0.051155 | 0.122049 | 0.113368 | 0.055937 | 0.120891 | 0.06096 |
| 5-Feb | 10 | 0.038132 | 0.022575 | 0.021962 | 0.098026 | 0.109067 | 0.118369 | 0.090868 | 0.027623 |
| >2005 | 13 | 0.015756 | 0.034555 | 0.020129 | 0.089669 | 0.078078 | 0.084971 | 0.089022 | 0.042916 |

- Furnace AFUE

To generate the regressions an AFUE of 0.95 was chosen for the upper limiting case and an AFUE of 0.70 was chosen for the lower limiting case. An AFUE of 0.78 was chosen for the 4 midpoint runs. AFUE was converted to the eQUEST input of HIR (Heating Input Ratio) based on a correlation from equation N2-42 on the Nonresidential ACM Manual, Section 2.5.2.10, Page 2-64 where:

HIR 	= (0.011116 * AFUE (80%) - 0.098185)-1

HIR	= 1.268

No useable data was found on which to base the distribution of furnace efficiencies throughout the SCE territory, however a value of 79.79 was provided by SCE [37] for average AFUE throughout the SCE territory. The values chosen for the efficiency range and probabilities are informed engineering estimates forming a normal distribution and resulting in the weighted average AFUE provided by SCE. These are shown in Table A10. The distribution of AFUE does not change from the base case to the QM case.

Table A10 Furnace AFUE and Probability

| Furnace AFUE | Probability |
| --- | --- |
| 0.70 | 0.1 |
| 0.74 | 0.2 |
| 0.78 | 0.4 |
| 0.865 | 0.2 |
| 0.95 | 0.1 |
| Average AFUE | .7980 |

- Shell UA

Shell UA is the factor that was chosen to represent the effect that vintage and climate zone have on the construction of a home. Shell UA is the inverse of the average R-Value of a home’s walls and roof multiplied by the surface area of the walls and roof with units of BTU/hr*F, so by multiplying UA by the difference between indoor and outdoor temperature the rate of heat transfer can be calculated. Shell UA was calculated for each vintage prototype in each climate zone. The UA includes wall, window and roof areas, excluding garages and floors. The areas of each type of exterior surface were from the 1978-1992 vintage prototypes. The UA was then calculated using the R-values for each vintage and climate zone from the DEER Residential Look-Up Table [24].  A separate infiltration UA was calculated based on the air changes specified in the DEER look-up table. Infiltration UA can be conceptualized as the rate of heat transfer due to infiltration as a function of outdoor to indoor temperature differential rather than a specific U-value and area. The Excel spreadsheet Vintage_Distribution_of_Home_Types [25] contains the combined shell and infiltration UA values for one and two story homes for each vintage in each climate zone. The resulting combined shell and infiltration UA values are the rate of heat transfer in BTU/hr through the walls and roof per degree Fahrenheit temperature difference between the outdoor air and indoor air.

To generate the regressions the DEER prototypes with the lowest and highest shell UAs were used for the upper and lower limiting cases. A prototype with a UA value near the middle of the range was selected for the midpoint runs.

An initial probability distribution of home types in each climate zone was based on information from RASS which is included with the spreadsheet Vintage Distribution of Home Types.xls [25]. For the expected value analysis the UA for each vintage of prototype was matched with the probability of each vintage occurring in each climate zone. Table A11 shows the vintage distribution of homes by climate zone.

Table A11 Vintage Distribution of Homes by Climate Zone

| Climate Zone | 6 | 8 | 9 | 10 | 13 | 14 | 15 | 16 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Vintage | 1-story | 1-story | 1-story | 1-story | 1-story | 1-story | 1-story | 1-story |
| Before 1978 | 0.93567 | 0.94477 | 0.89169 | 0.40567 | 0.3152 | 0.34972 | 0.28017 | 0.55340 |
| 1978-82 | 0.02546 | 0.01996 | 0.04060 | 0.11791 | 0.2817 | 0.20813 | 0.13454 | 0.05750 |
| 1983-1992 | 0.00885 | 0.02569 | 0.03648 | 0.27749 | 0.1047 | 0.20456 | 0.19197 | 0.20561 |
| 1993-2000 | 0.02845 | 0.00361 | 0.01148 | 0.07097 | 0.1492 | 0.03424 | 0.10638 | 0.05928 |
| 2001-2008 | 0.00157 | 0.00597 | 0.01975 | 0.12796 | 0.1492 | 0.20334 | 0.28694 | 0.12421 |
|  | 2-story | 2-story | 2-story | 2-story | 2-story | 2-story | 2-story | 2-story |
| Before 1978 | 0.76639 | 0.45252 | 0.32809 | 0.39496 | 0.2091 | 0.03378 | 0.33648 | 0.62363 |
| 1978-82 | 0.01481 | 0.07638 | 0.11650 | 0.05710 | 0.5210 | 0.21181 | 0.02971 | 0.07788 |
| 1983-1992 | 0.06809 | 0.23590 | 0.20410 | 0.19371 | 0.1737 | 0.39745 | 0.13321 | 0.15378 |
| 1993-2000 | 0.07458 | 0.10856 | 0.23599 | 0.11881 | 0.0481 | 0.02066 | 0.41195 | 0.08486 |
| 2001-2008 | 0.07614 | 0.12664 | 0.11531 | 0.23541 | 0.0481 | 0.33630 | 0.08864 | 0.05985 |

# Appendix B  eQUEST Simulation Model

## DOE2 eQUEST Energy Simulation Process

eQUEST [G, 9] is a DOE2 based simulation software package used to produce estimates of energy use of prototype residential building models.  DEER single family prototypes were used as the basis for all eQUEST simulations.  The single family prototype consists of two one-story houses and two two-story houses.  One house in each pair is rotated 90 degrees to capture the effect of orientation as shown in Figure B1.  The DEER database has separate prototypes for each of 6 vintages in each of the sixteen California climate zones. Each vintage has different values for building and system component properties based either on the current code or typical values.  Prototypes were developed for representative vintages to approximate the range of housing stock in SCE territory.  Prototypes were pulled from DEER and then run through eQUEST with TMY3 weather files and the three different thermostat schedules discussed under “Thermostat Setting,” in Appendix A. These thermostat schedules represent low, typical, and high set-point values to result in an appropriate range of conditions for the baseline simulation input files that were further modified for additional treatments.  Because the TMY3 weather file does not contain weather data for Mt. Shasta, an alternative weather site was selected for climate zone 16. Sandberg was selected because it is close to the same elevation as Mt Shasta and is located in SCE territory.  The TMY3 weather files also do not include the City of Sunnyvale, so the weather site at the City of San Jose International Airport was selected.  See Table B1 below for details.

Table B 1 TMY Weather City by SCE Climate Zone and HDD [26]

| California Climate Zone Number | TMY2 Weather City Name | TMY3 Weather City Name | TMY3 HDD |
| --- | --- | --- | --- |
| CZ-1 | Arcata | Arcata Airport | 4,802 |
| CZ-2 | Santa Rosa | Santa Rosa | 3,063 |
| CZ-3 | Oakland | Oakland Metropolitan Airport | 2,795 |
| CZ-4 | Sunnyvale | San Jose International Airport | 2,365 |
| CZ-5 | Santa Maria | Santa Maria Public Airport | 3,092 |
| CZ-11 | Red Bluff | Red Bluff Municipal Airport | 2,824 |
| CZ-12 | Sacramento | Sacramento Metropolitan | 2,647 |
| CZ-13 | Fresno | Fresno Yosemite Intl Airport | 2,325 |
| CZ-16 | Mt. Shasta | Sandberg | 6,650 |

To approximate shading on the houses, the DEER prototypes include a surface exterior to the houses, similar to a fence.  This surface is about 50% reflective and has a schedule for solar transmittance to simulate the variation in shading over the seasons.  Because only the lower floor is shaded, the solar effect was much greater on the two-story homes.  This difference led to some difficulty in creating regressions.  The shell UA does not account for solar effects, therefore UA showed an inconsistent effect on consumption between the one-story and two-story houses.  To resolve this, separate regressions were made for one-story and two-story homes.

# Appendix C  Design of Experiment

## Design of Experiment (DoEx) process

A software tool implementation, Design Expert [27], was used for this statistical process.  It results in a statistically valid regression model which accounts for the full range of treatment interactions.  DoEx software program uses statistical principles and equations to determine which factors and their interactions have statistically significant influence.  Then regression models were generated that were used to predict the response.  DoEx also estimates the magnitude of error in the results with common statistical indices such as R-square and coefficient of variation.  The adjusted R-square is a measure of how well the independent, or predictor, variables predict the dependent, or outcome, variable. A higher adjusted R-square indicates a better model; values can range from 0 to 1.  The standard deviation is sometimes expressed as a percent of the mean, in which case it's known as a coefficient of variation (CV).  The CV% is an indication of how much a given result is not explained by the regression, so a lower CV indicates a better model.  The adjusted R-square and CV% for the regressions used in this analysis are shown in Table C1. When creating a design, the user can optimize the tradeoff between accuracy and the number of runs (fewer runs means less accuracy) to meet the project’s budget and timeline.  During data analysis, the user selects which factors are included in the model and the program automatically displays the impact of these selections on the statistical indices.  Lastly, the program uses the selected factors to generate the regression model.

Table C 1 Regression Diagnostic Values

|  | 1-Story Homes |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Adjusted R2 |  |  | CV% |  |  |
| CZ | Energy | Demand | Gas | Energy | Demand | Gas |
| 6 | 0.972224 | 0.971404 | 0.972373 | 1.464756 | 6.289007 | 1.148847 |
| 8 | 0.983416 | 0.96415 | 0.968547 | 0.198182 | 6.521897 | 1.140865 |
| 9 | 0.977354 | 0.966845 | 0.973745 | 2.993777 | 5.813375 | 1.186026 |
| 10 | 0.971275 | 0.969535 | 0.97959 | 3.472063 | 6.868524 | 1.290585 |
| 13 | 0.979742 | 0.973067 | 0.98313 | 3.034517 | 4.41989 | 1.056654 |
| 14 | 0.977796 | 0.978402 | 0.982771 | 3.568311 | 3.419301 | 1.137612 |
| 15 | 0.969776 | 0.985867 | 0.969168 | 4.877248 | 2.475972 | 1.027821 |
| 16 | 0.979221 | 0.970877 | 0.973757 | 2.120943 | 5.674676 | 1.557696 |
|  | 2-Story Homes |  |  |  |  |  |
|  | Adjusted R2 |  |  | CV% |  |  |
| CZ | Energy | Demand | Gas | Energy | Demand | Gas |
| 6 | 0.990281 | 0.970471 | 0.977382 | 1.37036 | 5.78782 | 1.696418 |
| 8 | 0.992164 | 0.9802 | 0.974789 | 0.174605 | 2.82 | 1.699357 |
| 9 | 0.989511 | 0.982957 | 0.980665 | 2.168868 | 2.449195 | 1.620275 |
| 10 | 0.988037 | 0.986151 | 0.980063 | 2.36131 | 2.316584 | 1.820752 |
| 13 | 0.979526 | 0.985784 | 0.987631 | 3.122054 | 2.006759 | 1.380155 |
| 14 | 0.987611 | 0.984591 | 0.982876 | 2.715626 | 1.885455 | 1.710556 |
| 15 | 0.983306 | 0.989676 | 0.972611 | 3.530875 | 1.472637 | 1.636588 |
| 16 | 0.987422 | 0.985767 | 0.976912 | 1.907418 | 2.224488 | 2.026474 |

To begin, the relevant independent parameters are determined and each is assigned a low, typical and high value.  These are the factors that were defined for the Expected Value analysis.  The DoEx program then determines which combinations of parameters must be simulated to achieve a valid regression.  These combinations become the basis for specified interactive runs are made in eQUEST. The kWh, kW, and therm usage results are then entered back into the Design Expert tool, which then generates a regression model. In this way the number of runs is reduced but the resulting model is still statistically significant. Figure C 1 shows an example of how seven key parameters, each of which had each been assigned a range of three values, have resulted in the assignment of 68 simulation runs. The results of the runs were entered on the lines under the Response headings for kWh, kW, and therm to generate a regression model.  An example regression model is shown in Figure C1.  The full set of regressions is contained in the appended spreadsheet, Regressions. [28] The regression model has the additional advantage of being able to more accurately determine the results for the full value range of any parameter used in the regression.

Figure C 1 Example of Design of Experiments eQUEST Run Specification

Figure C2 shows how the results for total annual energy use and gas consumption varied for a set of 68 runs that were used to create the regressions for CZ 15.

Figure C 2 Results of 68 eQUEST Runs for Climate Zone 15

Figure C 3 Example Regression Equation

## Regression Check

To test the regressions a series of eQUEST runs were defined for climate zones 3, 5 and 13 to include disparate weather conditions.  Climate zone 3 represents a coastal climate; climate zone 5 represents a moderate climate; and climate zone 13 represents a hot climate.  Each of the EV factors used in the regressions was first assigned a range of values which included intermediate values not used in Design of Experiments.  A random number generator then picked a value for each factor, creating five different runs.  These eQUEST results were then compared to the predictions from the regressions for each climate zone.  The Excel spreadsheet titled Regression Check Results [29], show details of the eQUEST simulation inputs and results.

Table C2 below shows the comparison between the regression energy use and the eQUEST energy use, the percentage difference is 2.49% for kWh, 3.69% for kW, and 3.09% for therm.

Table C 2 Comparison of Regression Calculated Annual Energy Use to eQUEST Simulation Results

| Climate Zone | Random Selected Runs | Regression (kWh) | eQUEST (kWh) | Regression (kW) | eQUEST (kW) | Regression (therm) | eQUEST (therm) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3 | 1 | 8,209 | 7,944 | 3.33 | 4.3 | 1,571 | 1,598 |
|  | 2 | 9,656 | 9,561 | 5.39 | 5.43 | 1,847 | 1,900 |
|  | 3 | 7,718 | 8,086 | 2.78 | 2.99 | 1,505 | 1,549 |
|  | 4 | 9,560 | 9,596 | 5.25 | 5.46 | 1,994 | 2,092 |
|  | 5 | 7,793 | 8,087 | 3.27 | 3.12 | 1,513 | 1,528 |
| 5 | 1 | 8,320 | 8,730 | 3.05 | 3.77 | 1,633 | 1,606 |
|  | 2 | 10,262 | 9,836 | 4.95 | 4.95 | 1,944 | 2,011 |
|  | 3 | 7,267 | 6,830 | 2.7 | 2.85 | 1,722 | 1,778 |
|  | 4 | 9,942 | 8,569 | 4.84 | 4.55 | 2,198 | 2,160 |
|  | 5 | 7,636 | 8,098 | 2.93 | 2.78 | 1,604 | 1,630 |
| 13 | 1 | 13,104 | 11,820 | 5.99 | 5.32 | 1,339 | 1,374 |
|  | 2 | 11,055 | 11,202 | 5.09 | 4.83 | 1,360 | 1,403 |
|  | 3 | 18,087 | 17,433 | 8.16 | 9.09 | 1,679 | 1,848 |
|  | 4 | 14,901 | 14,977 | 7.6 | 9.04 | 1,467 | 1,596 |
|  | 5 | 14,111 | 12,932 | 6.78 | 6.29 | 1,401 | 1,469 |
|  | Average: | 10,508 | 10,247 | 4.81 | 4.98 | 1,652 | 1,703 |
|  | % Diff: |  | 2.49% |  | 3.69% |  | 3.09% |

# Appendix D – Quality maintenance factors

##### Step 1 - Derive the Quality Maintenance Factors

Table D1 shows the values of the EV factors for each zone which represent the expected value for the QM measure.

Table D1 Factors after QM Treatment from Expected Value Analysis

| One Story |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Post QM Factors | CZ_06 | CZ_08 | CZ_09 | CZ_10 | CZ_13 | CZ_14 | CZ_15 | CZ_16 |
| C_ShellUA | 738.96 | 758.99 | 764.82 | 658.95 | 515.88 | 599.75 | 532.71 | 562.90 |
| C_Tstat Offset | -2.198 | -2.198 | -2.198 | -2.198 | -2.198 | -2.198 | -2.198 | -2.198 |
| C_DuctUA | 236.42 | 236.42 | 236.42 | 236.42 | 236.42 | 236.42 | 236.42 | 236.42 |
| C_DuctLeak | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 |
| C_AFUE | 0.798 | 0.798 | 0.798 | 0.798 | 0.798 | 0.798 | 0.798 | 0.798 |
| C_RIF | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 |
| C_Nom_SEER | 10.05 | 10.10 | 10.06 | 10.02 | 10.23 | 10.25 | 10.27 | 10.13 |
| Two Story |  |  |  |  |  |  |  |  |
| Post QM Factors | CZ_06 | CZ_08 | CZ_09 | CZ_10 | CZ_13 | CZ_14 | CZ_15 | CZ_16 |
| C_ShellUA | 935.57 | 889.67 | 878.77 | 868.01 | 704.02 | 702.77 | 750.46 | 792.14 |
| C_Tstat Offset | -2.198 | -2.198 | -2.198 | -2.198 | -2.198 | -2.198 | -2.198 | -2.198 |
| C_DuctUA | 236.42 | 236.42 | 236.42 | 236.42 | 236.42 | 236.42 | 236.42 | 236.42 |
| C_DuctLeak | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 |
| C_AFUE | 0.798 | 0.798 | 0.798 | 0.798 | 0.798 | 0.798 | 0.798 | 0.798 |
| C_RIF | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 | 1.01 |
| C_Nom_SEER | 10.05 | 10.10 | 10.06 | 10.02 | 10.23 | 10.25 | 10.27 | 10.13 |

##### Step 2 - Convert the Factors into eQUEST Model Inputs

Factor 1: C_Shell UA

The as-treated QM shell-UA is matched to a prototype shell-UA as closely as possible, as shown in Table D2. This prototype is then modified to address the rest of the Factors.

Table D2 Factor Shell UA

| SINGLE story |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | CZ_06 | CZ_08 | CZ_09 | CZ_10 | CZ_13 | CZ_14 | CZ_15 | CZ_16 |
| Nearest Prototype UA to C_ShellUA | 748 | 768 | 768 | 647 | 507 | 599 | 533 | 563 |
| Vintage and CZ | V75 CZ06 | V75 CZ08 | V75 CZ09 | V85 CZ07 | V7 CZ10 | V85 CZ15 | V3 CZ03 | V96 CZ06 |
| Shell UA % Dif from C_ShellUA | 1.18% | 1.15% | 0.38% | 1.78% | 0.13% | 0.07% | 0.07% | 0.06% |
| TWO story |  |  |  |  |  |  |  |  |
|  | CZ_06 | CZ_08 | CZ_09 | CZ_10 | CZ_13 | CZ_14 | CZ_15 | CZ_16 |
| Nearest Prototype UA to C_ShellUA | 935 | 897 | 871 | 871 | 707 | 707 | 751 | 791 |
| Vintage and CZ | V75 CZ15 | V75 CZ01 | V85 CZ07 | V85 CZ07 | V3 CZ01 | V7 CZ10 | V3 CZ10 | V3 CZ09 |
| Shell UA % Dif from C_ShellUA | 0.05% | 0.86% | 0.84% | 0.39% | 0.47% | 0.65% | 0.12% | 0.18% |

Factor 2: Thermostat Schedule (C_Tstat Offset)

The post-QM EV of the thermostat offset is -2.198 or a cooling setpoint that on average is 2.198 degrees lower than the Title-24 thermostat for cooling. The sum of 24 hours of cooling setting for Title-24 is 1912 which is then divided by 24 to get an average setting of 79.7° F. So, a setting of 2.198° F lower F for cooling would be 77.5°. For heating the set point was set at 68.2° F.  The complete schedule is shown in the appended file. Tstat probability_v4 [22].

Factor 3: Duct Insulation (C_DuctUA)

There are two DEER prototype single family homes, 1-story and 2-story and each has both a supply duct and a return duct that are assumed to be insulated to the same R-value. The DuctUA factor was a combined value.

Table D3 Duct UA Factors

| DuctUA Factor | 277 | UA-values | Duct Areas |
| --- | --- | --- | --- |
| 1-story | Supply | 117 | 468 |
|  | Return | 22 | 87 |
| 2-story | Supply | 152 | 608 |
|  | Return | 87 | 346 |
| QM DuctUA Factor | 236.4 | QM-DuctUA input to eQUEST |  |
| 1-story | Supply | 99.8 | 468 |
|  | Return | 18.5 | 87 |
| 2-story | Supply | 129.7 | 608 |
|  | Return | 73.9 | 346 |
|  |  | Duct R-value | 4.7 |

For the homes with the QM treatments the Duct UA factor was determined to be 236.4, which is about 85% of the midpoint duct UA of 277. Using this ratio the eQUEST duct UA inputs were derived as shown in the table below. By dividing the new QM DuctUA values by the duct area indicates an average QM duct insulation R-value of 4.7.  The values used are shown above in Table D3

Factor 4: Duct Leakage (C_DuctLeak)

Duct leakage in eQUEST has to be split between the return and supply ducts.  Because some of the leaked supply air is assumed to eventually enter the conditioned space, a multiplier is used to adjust the supply leakage. In 1-story homes, the leakage multiplier is 75% and for the 2-story it is 67%. The QM DuctLeak Factor was 13.9% which is entered into eQUEST per Table D4.

Table D4 Duct Leakage Values

|  | Regression A |  | Return | Supply |
| --- | --- | --- | --- | --- |
|  | Total | 13.9% | 6.95% | 6.95% |
| 1-story | Multiplier to attic | 75% |  | 5.22% |
| 2-story | Multiplier to attic | 67% |  | 4.66% |

Factor 5: Gas Furnace AFUE (C_AFUE)

The gas furnace Annual Fuel Utilization Efficiency (AFUE) factor after QM was the same as the original input of about 80% because it is not a QM treatment. DEER used a conversion of AFUE to the eQUEST input of HIR (Heating Input Ratio) based on a correlation from equation N2-42 on the Nonresidential ACM Manual, Section 2.5.2.10, Page 2-64 where:

HIR 	= (0.011116 * AFUE (80%) - 0.098185)-1

HIR	= 1.268

This HIR value was used in all DEER single family prototypes.

Factor 6: Refrigeration Impact Factor (C_RIF)

The refrigeration impact factor represents corrections to the air conditioner compressor power, total cooling and sensible cooling capacity as a function of adjustments to refrigerant charge and air flow.  These are shown in Table D5.

The after-QM treatment value for C_RIF is 1.0109 which is used to derive the four eQUEST multipliers for:

- “Cooling-EIR impact fraction” that is taken times the rated compressor EIR (energy input ratio) that eQUEST uses to determine the power (kW) draw of the air conditioning compressor. The rated compressor EIR is determined by the SEER rating.

- “Cooling Capacity base fraction” which is taken times the base cooling capacity of the air conditioner.  eQUEST uses the modified total cooling capacity to determine the compressor runtime each hour as a fraction based on cooling load for the hour divided by the total cooling capacity.

- “Cool-sh-cap base fraction” is taken times the rated sensible cooling capacity that is determined as a fraction of the total capacity.

- “Typical CFM-ton” is the air flow associated with the system. The rated supply air flow of 400 CFM/Ton is adjusted down based on the RIF. So for the QM RIF of 1.010944 the DEER air flow is taken times 0.984 (393.7 / 400) to get the airflow after the QM treatments.

Table D5 Refrigeration Impact Factor

| RIF Refrig Impact Factor | Cooling-EIR base fraction | Cooling-Capacity base fraction | Cool-sh-cap base fraction | Typical CFM_ton |
| --- | --- | --- | --- | --- |
| 1.000 | 1.000 | 1.000 | 1.000 | 400.0 |
| 1.087 | 1.097 | 0.884 | 0.874 | 350.0 |
| 1.269 | 1.398 | 0.896 | 0.941 | 225.0 |

Factor 7: SEER (C_Nom_SEER)

SEER or Seasonal Energy Efficiency Ratio is the rating of HVAC equipment that determines how much electricity it uses to deliver cooling. The C_Nom_SEER after the QM treatment is the same as the SEER before the treatment since it is an equipment rating.  eQUEST needs to have the SEER converted to a EIR which is the inverse of the COP (coefficient of performance). The following equation was derived from Figure 5, Performance Characteristics of SEER-rated Cooling Systems” from EER & SEER as Predictors of Seasonal Cooling Performance by James J. Hirsch and Associates, December 15, 2003.

EER = 2.08 + 0.73 * SEER

The EER is then converted to EIR for input to eQUEST. SEER and EER are based on total electric power where EER is Cooling capacity (Btu/hr) divided by total electrical power in Watts. The eQUEST model has the blower and the condenser fan entered as separate items so the power for those two motors must be removed to get the proper EIRc based on compressor power only.

EER 	= Capacity / Total Power

Total Power = EER / Capacity = Comp + Blower + Condenser

Comp = (EER / Capacity) – Blower - Condenser

EIRc = Comp * 3.413 / Capacity

Where EIRc + EIR of the compressor only

EIRc = ((EER / Capacity) – Blower – Condenser) * 3.413 / Capacity

The EIRc is then modified by the RIF to get the final EIR value that is entered into eQUEST.

##### Step 3 – Perform the Simulations

The eQUEST models created were able to duplicate the electric energy use to within 10.9% on average.  The full results are shown in Table D6.  The results for kWh are also shown graphically in Figure D1.

Table D6 eQUEST v. Regression Comparison

| CZ | 6 | 8 | 9 | 10 | 13 | 14 | 15 | 16 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 Story Homes |  |  |  |  |  |  |  |
| kWh |  |  |  |  |  |  |  |  |
| eQUEST | 3899 | 4156 | 5946 | 5909 | 6701 | 8483 | 10971 | 5283 |
| Regression | 4857 | 5222 | 6750 | 6747 | 7520 | 8638 | 12406 | 5798 |
| % Difference | 19.7% | 20.4% | 11.9% | 12.4% | 10.9% | 1.8% | 11.6% | 8.9% |
| kW |  |  |  |  |  |  |  |  |
| eQUEST | 1.26 | 2.05 | 2.90 | 3.12 | 3.03 | 4.30 | 4.63 | 2.31 |
| Regression | 1.75 | 2.92 | 3.47 | 4.81 | 3.43 | 4.85 | 5.15 | 2.86 |
| % Difference | 28.1% | 29.8% | 16.4% | 35.1% | 11.7% | 11.4% | 10.1% | 19.3% |
| Therms |  |  |  |  |  |  |  |  |
| eQUEST | 1285 | 1257 | 1302 | 1277 | 1332 | 1386 | 910 | 1614 |
| Regression | 1335 | 1310 | 1334 | 1370 | 1353 | 1379 | 936 | 1667 |
| % Difference | 3.8% | 4.0% | 2.4% | 6.8% | 1.5% | 0.5% | 2.8% | 3.2% |
|  | 2 Story Homes |  |  |  |  |  |  |  |
| kWh |  |  |  |  |  |  |  |  |
| eQUEST | 9178 | 7749 | 11092 | 11132 | 13102 | 13416 | 19259 | 9597 |
| Regression | 8812 | 9530 | 11881 | 11994 | 13741 | 15708 | 22122 | 10462 |
| % Difference | 4.2% | 18.7% | 6.6% | 7.2% | 4.7% | 14.6% | 12.9% | 8.3% |
| kW |  |  |  |  |  |  |  |  |
| eQUEST | 3.43 | 3.77 | 5.46 | 6.50 | 5.25 | 6.77 | 7.75 | 4.07 |
| Regression | 3.11 | 4.41 | 5.32 | 6.16 | 5.92 | 7.67 | 8.99 | 4.75 |
| % Difference | 10.5% | 14.6% | 2.6% | 5.6% | 11.3% | 11.7% | 13.8% | 14.3% |
| Therms |  |  |  |  |  |  |  |  |
| eQUEST | 1458 | 1336 | 1340 | 1393 | 1447 | 1532 | 956 | 2032 |
| Regression | 1411 | 1359 | 1395 | 1449 | 1449 | 1487 | 986 | 1843 |
| % Difference | 3.4% | 1.7% | 3.9% | 3.8% | 0.1% | 3.1% | 3.1% | 10.3% |

Figure D1 Comparison of Results for One and Two Story Homes

# Appendix E – SCE/ED Application Types

| SCE Program Type | ED Application Type | 1st Baseline Savings | 2nd Baseline Savings | 1st Baseline Cost | 2nd Baseline Cost | 1st Baseline Life | 2nd Baseline Life |
| --- | --- | --- | --- | --- | --- | --- | --- |
| New | New Construction (Nc) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Replace on Burnout (ROB) | Replace on Burnout (Rob)/Normal Replacement (NR) | Above Code/Standard | N/A | Incremental Cost | N/A | EUL | 0 |
| Retrofit (RET) | Early Replacement (ER) | Above Cust. Existing | Above Code/Standard | Full Cost | Incremental Cost | RUL | EUL-RUL |
| Retrofit – First Baseline Only (REF) | Early Replacement RUL (ErRul) | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |
| Retrofit Add-on (REA) | N/A | Above Cust. Existing | N/A | Full Cost | N/A | EUL | 0 |

Bracketed letters refer to the Glossary and bracketed numbers refer to the References and Endnotes