## AnnlEnergy
RunID | BldgType | CZ | VintID | MeasureID | kWPkPer | kWhTotal | kWhLighting | kWhTaskLighting | kWhEquipment | kWhHeating | kWhCooling | kWhTower | kWhAux | kWhVentilation | kWhRefrigeration | kWhHPSupp | kWhSHW | kWhExterior | ThermTotal | ThermEquipment | ThermHeating | ThermSHW | MMBtuSrc | CoolCap | HeatCap | PctHrsZoneOutsideTR | PctHrsPlantNotSat | HrsZoneAbvCoolTR | HrsZoneBlwHeatTR | MMBtuSrc | HVAC | Elec Src MMBtu
OfS-w01-v14-AC_S1Std | OfS | CZ01 | 14 | AC_S1Std | 25.3837 | 89107.625 | 31593.9805 | 0 | 50648.0078 | 0 | 379.3268 | 0 | 0 | 6486.3589 | 0 | 0 | 0 | 0 | 716.1218 | 0 | 517.6463 | 198.4755 | 105.0424 | 158.9585 | -269.8495 | 0 | 0 | 0 | 0 | 105.0424 | 6865.6857 | 53.2777
OfS-w01-v14-AC_S0Std | OfS | CZ01 | 14 | AC_S0Std | 27.0094 | 91749.1406 | 31593.9805 | 0 | 50648.0078 | 0 | 3020.6204 | 0 | 0 | 6486.5811 | 0 | 0 | 0 | 0 | 715.7496 | 0 | 517.2755 | 198.4742 | 125.5034 | 160.6859 | -269.8567 | 0 | 0 | 0 | 0 | 125.5034 | 9507.2014 | 73.7759
OfS-w01-v14-AC_SHi | OfS | CZ01 | 14 | AC_SHi | 24.0266 | 85802.7422 | 31593.9805 | 0 | 50648.0078 | 0 | 274.6598 | 0 | 0 | 3286.1218 | 0 | 0 | 0 | 0 | 775.0664 | 0 | 576.5512 | 198.5152 | 85.2868 | 156.3029 | -270.305 | 0 | 0 | 0 | 0 | 85.2868 | 3560.7816 | 27.6317
OfS-w01-v14-AC_EStd | OfS | CZ01 | 14 | AC_EStd | 25.7229 | 87499.7969 | 31593.9805 | 0 | 50648.0078 | 0 | 400.7787 | 0 | 0 | 4857.0659 | 0 | 0 | 0 | 0 | 751.2358 | 0 | 552.734 | 198.5019 | 96.0743 | 157.1596 | -267.5881 | 0 | 0 | 0 | 0 | 96.0743 | 5257.8446 | 40.8009
OfS-w01-v14-AC_EHi | OfS | CZ01 | 14 | AC_EHi | 25.1266 | 87430.1094 | 31593.9805 | 0 | 50648.0078 | 0 | 331.0876 | 0 | 0 | 4857.0659 | 0 | 0 | 0 | 0 | 751.2358 | 0 | 552.734 | 198.5019 | 95.5335 | 157.1596 | -267.5881 | 0 | 0 | 0 | 0 | 95.5335 | 5188.1535 | 40.2601
OfS-w01-v14-PVAV_Std | OfS | CZ01 | 14 | PVAV_Std | 28.7278 | 88251.7031 | 31593.9805 | 0 | 50648.0078 | 43.7435 | 1675.3071 | 0 | 432.6949 | 3857.9429 | 0 | 0 | 0 | 0 | 813.08 | 0 | 615.1502 | 197.9296 | 108.1502 | 0 | 0 | 0 | 0 | 0 | 0 | 108.1502 | 6009.6884 | 46.6352
OfS-w01-v14-PVAV_Hi | OfS | CZ01 | 14 | PVAV_Hi | 27.2078 | 87877.2891 | 31593.9805 | 0 | 50648.0078 | 84.1362 | 1267.3765 | 0 | 436.227 | 3847.5293 | 0 | 0 | 0 | 0 | 637.3453 | 0 | 439.4049 | 197.9404 | 87.6702 | 0 | 0 | 0 | 0 | 0 | 0 | 87.6702 | 5635.269 | 43.7297
OfS-w01-v14-VRF_HP_OAU0 | OfS | CZ01 | 14 | VRF_HP_OAU0 | 26.164 | 93941.7656 | 31593.9805 | 0 | 50648.0078 | 4275.48 | 3095.3481 | 0 | 0 | 4329.0386 | 0 | 0 | 0 | 0 | 198.4423 | 0 | 0 | 198.4423 | 90.791 | 192.2978 | -201.0131 | 0 | 0 | 0 | 0 | 90.791 | 11699.8667 | 90.791
OfS-w01-v14-VRF_HP_OAU1 | OfS | CZ01 | 14 | VRF_HP_OAU1 | 25.6628 | 93202.3438 | 31593.9805 | 0 | 50648.0078 | 3881.4128 | 2750.001 | 0 | 0 | 4329.0386 | 0 | 0 | 0 | 0 | 198.4423 | 0 | 0 | 198.4423 | 85.0531 | 192.2978 | -201.0131 | 0 | 0 | 0 | 0 | 85.0531 | 10960.4524 | 85.0531
OfS-w01-v14-VRF_HP_OAU2 | OfS | CZ01 | 14 | VRF_HP_OAU2 | 25.1979 | 92566.7969 | 31593.9805 | 0 | 50648.0078 | 3534.7783 | 2461.0686 | 0 | 0 | 4329.0386 | 0 | 0 | 0 | 0 | 198.4423 | 0 | 0 | 198.4423 | 80.1211 | 192.2978 | -201.0131 | 0 | 0 | 0 | 0 | 80.1211 | 10324.8855 | 80.1211
OfS-w01-v14-VRF_HR_OAU0 | OfS | CZ01 | 14 | VRF_HR_OAU0 | 26.0643 | 93061.2188 | 31593.9805 | 0 | 50648.0078 | 3514.105 | 2968.8826 | 0 | 0 | 4336.3081 | 0 | 0 | 0 | 0 | 198.445 | 0 | 0 | 198.445 | 83.9577 | 191.0489 | -199.7387 | 0 | 0 | 0 | 0 | 83.9577 | 10819.2957 | 83.9577
OfS-w01-v14-VRF_HR_OAU1 | OfS | CZ01 | 14 | VRF_HR_OAU1 | 25.6007 | 92404.4141 | 31593.9805 | 0 | 50648.0078 | 3178.9106 | 2647.2739 | 0 | 0 | 4336.3081 | 0 | 0 | 0 | 0 | 198.445 | 0 | 0 | 198.445 | 78.8609 | 191.0489 | -199.7387 | 0 | 0 | 0 | 0 | 78.8609 | 10162.4927 | 78.8609
OfS-w01-v14-VRF_HR_OAU2 | OfS | CZ01 | 14 | VRF_HR_OAU2 | 25.202 | 91818.6797 | 31593.9805 | 0 | 50648.0078 | 2881.146 | 2359.3074 | 0 | 0 | 4336.3081 | 0 | 0 | 0 | 0 | 198.445 | 0 | 0 | 198.445 | 74.3157 | 191.0489 | -199.7387 | 0 | 0 | 0 | 0 | 74.3157 | 9576.7615 | 74.3157
OfL-w01-v14-FPFC_1 | OfL | CZ01 | 14 | FPFC_1 | 433.5292 | 1613998.875 | 500422.4062 | 0 | 883691.5 | 510.6809 | 115525.6797 | 1832.0542 | 44950.6719 | 67067.5625 | 0 | 0 | 0 | 0 | 10076.7674 | 0 | 6737.8342 | 3338.9341 | 2443.4871 | 2466.8813 | -6039.0566 | 0 | 0 | 0 | 0 | 2443.4871 | 228054.595 | 1769.7037
OfL-w01-v14-FPFC_2 | OfL | CZ01 | 14 | FPFC_2 | 415.1813 | 1583070.75 | 500422.4062 | 0 | 883691.5 | 1108.9432 | 83134 | 3170.9778 | 44756.4141 | 66788.3828 | 0 | 0 | 0 | 0 | 7686.4979 | 0 | 4347.4989 | 3338.9997 | 1954.0628 | 2466.8813 | -6039.0566 | 0 | 0 | 0 | 0 | 1954.0628 | 195787.7401 | 1519.3129
OfL-w01-v14-VRF_HP_OAU0 | OfL | CZ01 | 14 | VRF_HP_OAU0 | 438.3591 | 1572293.75 | 500422.4062 | 0 | 883691.5 | 25055.3125 | 89263.1484 | 0 | 213.4769 | 73650.0469 | 0 | 0 | 0 | 0 | 3338.9286 | 0 | 0 | 3338.9286 | 1460.2922 | 3422.2825 | -3577.9819 | 0 | 0 | 0 | 0 | 1460.2922 | 188181.9847 | 1460.2922
OfL-w01-v14-VRF_HP_OAU1 | OfL | CZ01 | 14 | VRF_HP_OAU1 | 420.0178 | 1553170.875 | 500422.4062 | 0 | 883691.5 | 21625.4355 | 73569.8906 | 0 | 213.4769 | 73650.0469 | 0 | 0 | 0 | 0 | 3338.9286 | 0 | 0 | 3338.9286 | 1311.8967 | 3422.2825 | -3577.9819 | 0 | 0 | 0 | 0 | 1311.8967 | 169058.8499 | 1311.8967
OfL-w01-v14-VRF_HP_OAU2 | OfL | CZ01 | 14 | VRF_HP_OAU2 | 409.5473 | 1542469.25 | 500422.4062 | 0 | 883691.5 | 19585.6504 | 64908.1836 | 0 | 213.4769 | 73650.0469 | 0 | 0 | 0 | 0 | 3338.9286 | 0 | 0 | 3338.9286 | 1228.8531 | 3422.2825 | -3577.9819 | 0 | 0 | 0 | 0 | 1228.8531 | 158357.3577 | 1228.8531
OfL-w01-v14-VRF_HR_OAU0 | OfL | CZ01 | 14 | VRF_HR_OAU0 | 436.3544 | 1563456.25 | 500422.4062 | 0 | 883691.5 | 20754.834 | 84333.5078 | 0 | 213.4769 | 74042.4688 | 0 | 0 | 0 | 0 | 3338.9254 | 0 | 0 | 3338.9254 | 1391.7117 | 3430.5359 | -3586.7759 | 0 | 0 | 0 | 0 | 1391.7117 | 179344.2874 | 1391.7117
OfL-w01-v14-VRF_HR_OAU1 | OfL | CZ01 | 14 | VRF_HR_OAU1 | 418.3131 | 1545688.875 | 500422.4062 | 0 | 883691.5 | 17793.5469 | 69527.6172 | 0 | 213.4769 | 74042.4688 | 0 | 0 | 0 | 0 | 3338.9254 | 0 | 0 | 3338.9254 | 1253.8384 | 3430.5359 | -3586.7759 | 0 | 0 | 0 | 0 | 1253.8384 | 161577.1097 | 1253.8384
OfL-w01-v14-VRF_HR_OAU2 | OfL | CZ01 | 14 | VRF_HR_OAU2 | 407.1448 | 1536101.5 | 500422.4062 | 0 | 883691.5 | 16067.3896 | 61666.4648 | 0 | 213.4769 | 74042.4688 | 0 | 0 | 0 | 0 | 3338.9254 | 0 | 0 | 3338.9254 | 1179.4408 | 3430.5359 | -3586.7759 | 0 | 0 | 0 | 0 | 1179.4408 | 151989.8001 | 1179.4408
EPr-w01-v14-AC_S1Std | EPr | CZ01 | 14 | AC_S1Std | 101.0438 | 277371.4062 | 133157.6562 | 0 | 99493.7734 | 0 | 1805.2543 | 0 | 0 | 42914.9062 | 0 | 0 | 0 | 0 | 16842.9926 | 110.3944 | 14282.5805 | 2450.0213 | 1775.2865 | 893.0835 | -2430.1016 | 0 | 0 | 0 | 0 | 1775.2865 | 44720.1605 | 347.0284
EPr-w01-v14-AC_S0Std | EPr | CZ01 | 14 | AC_S0Std | 101.5844 | 277689.0625 | 133157.6562 | 0 | 99493.7734 | 0 | 2122.8708 | 0 | 0 | 42914.9141 | 0 | 0 | 0 | 0 | 16842.9722 | 110.3944 | 14282.5587 | 2450.0213 | 1777.7491 | 893.0894 | -2430.1064 | 0 | 0 | 0 | 0 | 1777.7491 | 45037.7849 | 349.4932
EPr-w01-v14-AC_SHi | EPr | CZ01 | 14 | AC_SHi | 94.7948 | 266385.9375 | 133157.6562 | 0 | 99493.7734 | 0 | 1322.4586 | 0 | 0 | 32412.1094 | 0 | 0 | 0 | 0 | 17209.801 | 110.3944 | 14649.2339 | 2450.1685 | 1726.7036 | 871.7748 | -2430.3176 | 0 | 0 | 0 | 0 | 1726.7036 | 33734.568 | 261.7802
EPr-w01-v14-AC_EStd | EPr | CZ01 | 14 | AC_EStd | 102.9483 | 275669 | 133157.6562 | 0 | 99493.7734 | 0 | 1910.2697 | 0 | 0 | 41107.5781 | 0 | 0 | 0 | 0 | 16869.9904 | 110.3944 | 14309.4426 | 2450.1528 | 1764.7628 | 887.1598 | -2417.1892 | 0 | 0 | 0 | 0 | 1764.7628 | 43017.8478 | 333.8185
EPr-w01-v14-AC_EHi | EPr | CZ01 | 14 | AC_EHi | 100.4078 | 275336.8438 | 133157.6562 | 0 | 99493.7734 | 0 | 1578.0941 | 0 | 0 | 41107.5781 | 0 | 0 | 0 | 0 | 16869.9904 | 110.3944 | 14309.4426 | 2450.1528 | 1762.1851 | 887.1598 | -2417.1892 | 0 | 0 | 0 | 0 | 1762.1851 | 42685.6722 | 331.2408
EPr-w01-v14-PVAV_Std | EPr | CZ01 | 14 | PVAV_Std | 112.202 | 287817.4375 | 133157.6562 | 0 | 99493.7734 | 370.4468 | 6904.1572 | 0 | 805.7947 | 47085.7266 | 0 | 0 | 0 | 0 | 16779.6454 | 110.3944 | 14218.8698 | 2450.3859 | 1849.9761 | 955.6633 | -956.8256 | 0 | 0 | 0 | 0 | 1849.9761 | 55166.1253 | 428.0891
EPr-w01-v14-PVAV_Hi | EPr | CZ01 | 14 | PVAV_Hi | 106.2448 | 285650.4688 | 133157.6562 | 0 | 99493.7734 | 740.9379 | 5123.3906 | 0 | 829.6933 | 46305.1445 | 0 | 0 | 0 | 0 | 15822.0979 | 110.3944 | 13261.1635 | 2450.5402 | 1737.3899 | 938.5379 | -955.4597 | 0 | 0 | 0 | 0 | 1737.3899 | 52999.1663 | 411.2735
EPr-w01-v14-VRF_HP_OAU0 | EPr | CZ01 | 14 | VRF_HP_OAU0 | 107.1133 | 365247.5625 | 133157.6562 | 0 | 99493.7734 | 82057.8828 | 2238.5308 | 0 | 0 | 48299.9297 | 0 | 0 | 0 | 0 | 2560.1621 | 110.3944 | 0 | 2449.767 | 1028.9476 | 928.844 | -971.2048 | 0.42033 | 0 | 0 | 11 | 1028.9476 | 132596.3433 | 1028.9476
EPr-w01-v14-VRF_HP_OAU1 | EPr | CZ01 | 14 | VRF_HP_OAU1 | 104.9332 | 357245.125 | 133157.6562 | 0 | 99493.7734 | 74316.8906 | 1977.3274 | 0 | 0 | 48299.9297 | 0 | 0 | 0 | 0 | 2560.1621 | 110.3944 | 0 | 2449.767 | 966.8506 | 928.844 | -971.2048 | 0.42033 | 0 | 0 | 11 | 966.8506 | 124594.1477 | 966.8506
EPr-w01-v14-VRF_HP_OAU2 | EPr | CZ01 | 14 | VRF_HP_OAU2 | 103.3597 | 350175.6562 | 133157.6562 | 0 | 99493.7734 | 67464.2422 | 1760.4717 | 0 | 0 | 48299.9297 | 0 | 0 | 0 | 0 | 2560.1621 | 110.3944 | 0 | 2449.767 | 911.9912 | 928.844 | -971.2048 | 0.42033 | 0 | 0 | 11 | 911.9912 | 117524.6436 | 911.9912
EPr-w01-v14-VRF_HR_OAU0 | EPr | CZ01 | 14 | VRF_HR_OAU0 | 105.1705 | 353799.1562 | 133157.6562 | 0 | 99493.7734 | 70764.0078 | 2072.9097 | 0 | 0 | 48311.0156 | 0 | 0 | 0 | 0 | 2560.1669 | 110.3944 | 0 | 2449.7725 | 940.108 | 912.9493 | -954.4016 | 1.3374 | 0 | 0 | 35 | 940.108 | 121147.9331 | 940.108
EPr-w01-v14-VRF_HR_OAU1 | EPr | CZ01 | 14 | VRF_HR_OAU1 | 103.5775 | 346651.3438 | 133157.6562 | 0 | 99493.7734 | 63853.4102 | 1835.8252 | 0 | 0 | 48311.0156 | 0 | 0 | 0 | 0 | 2560.1669 | 110.3944 | 0 | 2449.7725 | 884.6419 | 912.9431 | -954.3951 | 1.3374 | 0 | 0 | 35 | 884.6419 | 114000.251 | 884.6419
EPr-w01-v14-VRF_HR_OAU2 | EPr | CZ01 | 14 | VRF_HR_OAU2 | 102.1859 | 340454.9688 | 133157.6562 | 0 | 99493.7734 | 57858.0391 | 1634.9232 | 0 | 0 | 48311.0156 | 0 | 0 | 0 | 0 | 2560.1669 | 110.3944 | 0 | 2449.7725 | 836.5589 | 912.9372 | -954.3889 | 1.3374 | 0 | 0 | 35 | 836.5589 | 107803.9779 | 836.5589
Htl-w01-v14-FPFC_1 | Htl | CZ01 | 14 | FPFC_1 | 458.7003 | 3048060.75 | 566447.625 | 0 | 1692748 | 13066.3545 | 220444.6875 | 3303.0891 | 143202.375 | 408848 | 0 | 0 | 0 | 0 | 224773.2019 | 0 | 179925.8522 | 44847.2883 | 24088.5418 | 4965.0791 | -10164.4141 | 0 | 0 | 0 | 0 | 24088.5418 | 785561.417 | 6095.9566
Htl-w01-v14-FPFC_2 | Htl | CZ01 | 14 | FPFC_2 | 424.276 | 2955900.1372 | 566447.625 | 0 | 1692748 | 23845.8785 | 155866.2483 | 5876.374 | 143178.4299 | 413061.9063 | 0 | 0 | 0 | 0 | 197674.8556 | 0 | 153660.5896 | 44847.484 | 20924.6922 | 4965.0791 | -10164.4141 | 0 | 0 | 0 | 0 | 20924.6922 | 735952.463 | 5710.9911 | 0
Htl-w01-v14-VRF_HP_OAU0 | Htl | CZ01 | 14 | VRF_HP_OAU0 | 440.3357 | 3981387.5 | 566447.625 | 0 | 1692748 | 1209171.375 | 94976.8828 | 0 | 1121.6216 | 416920.9375 | 0 | 0 | 0 | 0 | 44847.5648 | 0 | 0 | 44847.5648 | 13364.2007 | 5258.0396 | -5467.249 | 0.045657 | 0 | 1 | 3 | 13364.2007 | 1722190.8169 | 13364.2007
Htl-w01-v14-VRF_HP_OAU1 | Htl | CZ01 | 14 | VRF_HP_OAU1 | 424.7982 | 3839662.75 | 566447.625 | 0 | 1692748 | 1081819.375 | 80604.8047 | 0 | 1121.6216 | 416920.875 | 0 | 0 | 0 | 0 | 44847.5648 | 0 | 0 | 44847.5648 | 12264.4214 | 5258.0239 | -5467.2324 | 0.045657 | 0 | 1 | 3 | 12264.4214 | 1580466.6763 | 12264.4214
Htl-w01-v14-VRF_HP_OAU2 | Htl | CZ01 | 14 | VRF_HP_OAU2 | 413.1888 | 3723684 | 566447.625 | 0 | 1692748 | 976314 | 70131.2656 | 0 | 1121.6216 | 416920.875 | 0 | 0 | 0 | 0 | 44847.5648 | 0 | 0 | 44847.5648 | 11364.425 | 5258.0093 | -5467.2168 | 0.045657 | 0 | 1 | 3 | 11364.425 | 1464487.7622 | 11364.425
Htl-w01-v14-VRF_HR_OAU0 | Htl | CZ01 | 14 | VRF_HR_OAU0 | 435.3592 | 3842653 | 566447.625 | 0 | 1692748 | 1075220 | 89759.9453 | 0 | 1121.6216 | 417355.5625 | 0 | 0 | 0 | 0 | 44847.6518 | 0 | 0 | 44847.6518 | 12287.6273 | 5236.7393 | -5445.1504 | 1.0501 | 0 | 67 | 25 | 12287.6273 | 1583457.1294 | 12287.6273
Htl-w01-v14-VRF_HR_OAU1 | Htl | CZ01 | 14 | VRF_HR_OAU1 | 420.6089 | 3713791 | 566447.625 | 0 | 1692748 | 959847 | 76270.375 | 0 | 1121.6216 | 417355.5312 | 0 | 0 | 0 | 0 | 44847.6518 | 0 | 0 | 44847.6518 | 11287.6535 | 5236.7031 | -5445.1123 | 1.0501 | 0 | 67 | 25 | 11287.6535 | 1454594.5278 | 11287.6535
Htl-w01-v14-VRF_HR_OAU2 | Htl | CZ01 | 14 | VRF_HR_OAU2 | 409.9117 | 3607963.5 | 566447.625 | 0 | 1692748 | 863879.375 | 66410.8672 | 0 | 1121.6216 | 417355.5312 | 0 | 0 | 0 | 0 | 44847.6518 | 0 | 0 | 44847.6518 | 10466.435 | 5236.6685 | -5445.0767 | 1.0501 | 0 | 67 | 25 | 10466.435 | 1348767.395 | 10466.435
OfS-w02-v14-AC_S1Std | OfS | CZ02 | 14 | AC_S1Std | 39.1715 | 99246.1094 | 31593.9805 | 0 | 50648.0078 | 0 | 8182.3511 | 0 | 0 | 8821.8584 | 0 | 0 | 0 | 0 | 421.998 | 0 | 236.5244 | 185.4737 | 155.6051 | 256.6566 | -378.1434 | 0 | 0 | 0 | 0 | 155.6051 | 17004.2095 | 131.9527
OfS-w02-v14-AC_S0Std | OfS | CZ02 | 14 | AC_S0Std | 39.1729 | 102745.1797 | 31593.9805 | 0 | 50648.0078 | 0 | 11681.6055 | 0 | 0 | 8821.6523 | 0 | 0 | 0 | 0 | 421.7937 | 0 | 236.321 | 185.4727 | 182.7374 | 256.6782 | -378.1329 | 0 | 0 | 0 | 0 | 182.7374 | 20503.2578 | 159.1053
OfS-w02-v14-AC_SHi | OfS | CZ02 | 14 | AC_SHi | 35.2189 | 93188.2891 | 31593.9805 | 0 | 50648.0078 | 0 | 6428.3506 | 0 | 0 | 4518.0347 | 0 | 0 | 0 | 0 | 452.138 | 0 | 266.5959 | 185.5421 | 111.6035 | 255.864 | -320.1088 | 0 | 0 | 0 | 0 | 111.6035 | 10946.3853 | 84.9439
OfS-w02-v14-AC_EStd | OfS | CZ02 | 14 | AC_EStd | 40.7419 | 97817.625 | 31593.9805 | 0 | 50648.0078 | 0 | 8613.6611 | 0 | 0 | 6962.0791 | 0 | 0 | 0 | 0 | 433.9142 | 0 | 248.3891 | 185.525 | 145.7067 | 254.2805 | -316.6555 | 0 | 0 | 0 | 0 | 145.7067 | 15575.7402 | 120.8677
OfS-w02-v14-AC_EHi | OfS | CZ02 | 14 | AC_EHi | 37.6873 | 96319.7812 | 31593.9805 | 0 | 50648.0078 | 0 | 7115.8379 | 0 | 0 | 6962.0791 | 0 | 0 | 0 | 0 | 433.9142 | 0 | 248.3891 | 185.525 | 134.0835 | 254.2805 | -316.6555 | 0 | 0 | 0 | 0 | 134.0835 | 14077.917 | 109.2446
OfS-w02-v14-PVAV_Std | OfS | CZ02 | 14 | PVAV_Std | 43.1525 | 99318.9062 | 31593.9805 | 0 | 50648.0078 | 24.4212 | 12676.1006 | 0 | 326.249 | 4050.1692 | 0 | 0 | 0 | 0 | 524.7548 | 0 | 339.3421 | 185.4129 | 166.4513 | 0 | 0 | 0 | 0 | 0 | 0 | 166.4513 | 17076.94 | 132.5171
OfS-w02-v14-PVAV_Hi | OfS | CZ02 | 14 | PVAV_Hi | 38.1535 | 96312.5781 | 31593.9805 | 0 | 50648.0078 | 46.509 | 9662.3223 | 0 | 327.2704 | 4034.5044 | 0 | 0 | 0 | 0 | 419.9101 | 0 | 234.492 | 185.4182 | 132.6371 | 0 | 0 | 0 | 0 | 0 | 0 | 132.6371 | 14070.6061 | 109.1879
OfS-w02-v14-VRF_HP_OAU0 | OfS | CZ02 | 14 | VRF_HP_OAU0 | 38.5875 | 100233.4766 | 31593.9805 | 0 | 50648.0078 | 2258.0845 | 11086.4121 | 0 | 0 | 4647.0903 | 0 | 0 | 0 | 0 | 185.4687 | 0 | 0 | 185.4687 | 139.6147 | 248.8797 | -260.1894 | 0 | 0 | 0 | 0 | 139.6147 | 17991.5869 | 139.6147
OfS-w02-v14-VRF_HP_OAU1 | OfS | CZ02 | 14 | VRF_HP_OAU1 | 36.5264 | 98737.8359 | 31593.9805 | 0 | 50648.0078 | 2053.7354 | 9795.1338 | 0 | 0 | 4647.0903 | 0 | 0 | 0 | 0 | 185.4687 | 0 | 0 | 185.4687 | 128.0086 | 248.8797 | -260.1894 | 0 | 0 | 0 | 0 | 128.0086 | 16495.9595 | 128.0086
OfS-w02-v14-VRF_HP_OAU2 | OfS | CZ02 | 14 | VRF_HP_OAU2 | 34.8006 | 97465.6406 | 31593.9805 | 0 | 50648.0078 | 1872.1362 | 8704.5225 | 0 | 0 | 4647.0903 | 0 | 0 | 0 | 0 | 185.4687 | 0 | 0 | 185.4687 | 118.1363 | 248.8797 | -260.1894 | 0 | 0 | 0 | 0 | 118.1363 | 15223.749 | 118.1363
OfS-w02-v14-VRF_HR_OAU0 | OfS | CZ02 | 14 | VRF_HR_OAU0 | 38.2281 | 99037.8281 | 31593.9805 | 0 | 50648.0078 | 1877.6206 | 10275.7432 | 0 | 0 | 4642.5913 | 0 | 0 | 0 | 0 | 185.4552 | 0 | 0 | 185.4552 | 130.3366 | 247.916 | -259.181 | 0 | 0 | 0 | 0 | 130.3366 | 16795.9551 | 130.3366
OfS-w02-v14-VRF_HR_OAU1 | OfS | CZ02 | 14 | VRF_HR_OAU1 | 36.085 | 97696.4766 | 31593.9805 | 0 | 50648.0078 | 1700.8121 | 9111.1865 | 0 | 0 | 4642.5913 | 0 | 0 | 0 | 0 | 185.4552 | 0 | 0 | 185.4552 | 119.9276 | 247.916 | -259.181 | 0 | 0 | 0 | 0 | 119.9276 | 15454.59 | 119.9276
OfS-w02-v14-VRF_HR_OAU2 | OfS | CZ02 | 14 | VRF_HR_OAU2 | 34.3452 | 96548.0938 | 31593.9805 | 0 | 50648.0078 | 1547.9126 | 8115.7124 | 0 | 0 | 4642.5913 | 0 | 0 | 0 | 0 | 185.4552 | 0 | 0 | 185.4552 | 111.0162 | 247.916 | -259.181 | 0 | 0 | 0 | 0 | 111.0162 | 14306.2163 | 111.0162
OfL-w02-v14-FPFC_1 | OfL | CZ02 | 14 | FPFC_1 | 509.712 | 1754176.375 | 500422.4062 | 0 | 883691.5 | 420.8656 | 217838.0938 | 3898.8862 | 73538.2734 | 74367.9141 | 0 | 0 | 0 | 0 | 8500.7859 | 0 | 5394.6714 | 3106.1149 | 3380.9087 | 4091.9614 | -8264.9365 | 0 | 0 | 0 | 0 | 3380.9087 | 366165.1469 | 2841.4415
OfL-w02-v14-FPFC_2 | OfL | CZ02 | 14 | FPFC_2 | 484.0682 | 1700038.25 | 500422.4062 | 0 | 883691.5 | 896.3759 | 159338.3125 | 8098.4888 | 73233.3516 | 74359.1172 | 0 | 0 | 0 | 0 | 6093.2608 | 0 | 2987.0998 | 3106.1597 | 2687.4487 | 4091.9614 | -8264.9365 | 0 | 0 | 0 | 0 | 2687.4487 | 307827.1571 | 2388.7387
OfL-w02-v14-VRF_HP_OAU0 | OfL | CZ02 | 14 | VRF_HP_OAU0 | 640.9734 | 1706650.125 | 500422.4062 | 0 | 883691.5 | 13596.6855 | 223689.9844 | 0 | 213.4769 | 85037.3594 | 0 | 0 | 0 | 0 | 3105.6922 | 0 | 0 | 3105.6922 | 2502.891 | 4449.811 | -4652.3506 | 0 | 0 | 0 | 0 | 2502.891 | 322537.5062 | 2502.891
OfL-w02-v14-VRF_HP_OAU1 | OfL | CZ02 | 14 | VRF_HP_OAU1 | 585.6895 | 1665167.75 | 500422.4062 | 0 | 883691.5 | 11714.9004 | 184089.4844 | 0 | 213.4769 | 85037.3594 | 0 | 0 | 0 | 0 | 3105.6922 | 0 | 0 | 3105.6922 | 2180.9885 | 4449.811 | -4652.3506 | 0 | 0 | 0 | 0 | 2180.9885 | 281055.221 | 2180.9885
OfL-w02-v14-VRF_HP_OAU2 | OfL | CZ02 | 14 | VRF_HP_OAU2 | 555.5587 | 1642262.375 | 500422.4062 | 0 | 883691.5 | 10613.7021 | 162285.2812 | 0 | 213.4769 | 85037.3594 | 0 | 0 | 0 | 0 | 3105.6922 | 0 | 0 | 3105.6922 | 2003.2426 | 4449.811 | -4652.3506 | 0 | 0 | 0 | 0 | 2003.2426 | 258149.8196 | 2003.2426
OfL-w02-v14-VRF_HR_OAU0 | OfL | CZ02 | 14 | VRF_HR_OAU0 | 646.5062 | 1691293.5 | 500422.4062 | 0 | 883691.5 | 11351.3027 | 209101.8438 | 0 | 213.4769 | 86514.4844 | 0 | 0 | 0 | 0 | 3105.6765 | 0 | 0 | 3105.6765 | 2383.7254 | 4592.4668 | -4801.2891 | 0 | 0 | 0 | 0 | 2383.7254 | 307181.1077 | 2383.7254
OfL-w02-v14-VRF_HR_OAU1 | OfL | CZ02 | 14 | VRF_HR_OAU1 | 591.2188 | 1652487.75 | 500422.4062 | 0 | 883691.5 | 9687.0674 | 171960.6094 | 0 | 213.4769 | 86514.4844 | 0 | 0 | 0 | 0 | 3105.6765 | 0 | 0 | 3105.6765 | 2082.595 | 4592.4668 | -4801.2891 | 0 | 0 | 0 | 0 | 2082.595 | 268375.638 | 2082.595
OfL-w02-v14-VRF_HR_OAU2 | OfL | CZ02 | 14 | VRF_HR_OAU2 | 560.7246 | 1631300.625 | 500422.4062 | 0 | 883691.5 | 8729.209 | 151731.375 | 0 | 213.4769 | 86514.4844 | 0 | 0 | 0 | 0 | 3105.6765 | 0 | 0 | 3105.6765 | 1918.1831 | 4592.4668 | -4801.2891 | 0 | 0 | 0 | 0 | 1918.1831 | 247188.5452 | 1918.1831
EPr-w02-v14-AC_S1Std | EPr | CZ02 | 14 | AC_S1Std | 1.7037 | 317011.0938 | 133157.6562 | 0 | 99493.7734 | 0 | 28621.0938 | 0 | 0 | 55738.582 | 0 | 0 | 0 | 0 | 11242.4794 | 110.3944 | 8845.7997 | 2286.284 | 1539.2111 | 1602.4835 | -3384.1475 | 0 | 0 | 0 | 0 | 1539.2111 | 84359.6758 | 654.6311
EPr-w02-v14-AC_S0Std | EPr | CZ02 | 14 | AC_S0Std | 1.7038 | 321547.375 | 133157.6562 | 0 | 99493.7734 | 0 | 33157.1836 | 0 | 0 | 55738.9258 | 0 | 0 | 0 | 0 | 11242.313 | 110.3944 | 8845.632 | 2286.2834 | 1574.397 | 1602.4868 | -3384.1543 | 0 | 0 | 0 | 0 | 1574.397 | 88896.1094 | 689.8338
EPr-w02-v14-AC_SHi | EPr | CZ02 | 14 | AC_SHi | 1.6875 | 294714.2812 | 133157.6562 | 0 | 99493.7734 | 0 | 22384.2949 | 0 | 0 | 39678.7031 | 0 | 0 | 0 | 0 | 11367.5328 | 110.3944 | 8970.6931 | 2286.4456 | 1378.6782 | 1572.5137 | -2757.9324 | 0 | 0 | 0 | 0 | 1378.6782 | 62062.998 | 481.6089
EPr-w02-v14-AC_EStd | EPr | CZ02 | 14 | AC_EStd | 1.7177 | 317344.1875 | 133157.6562 | 0 | 99493.7734 | 0 | 30652.9863 | 0 | 0 | 54039.6836 | 0 | 0 | 0 | 0 | 11073.7216 | 110.3944 | 8676.9024 | 2286.4229 | 1524.9054 | 1637.2334 | -2823.1543 | 0 | 0 | 0 | 0 | 1524.9054 | 84692.6699 | 657.2151
EPr-w02-v14-AC_EHi | EPr | CZ02 | 14 | AC_EHi | 1.7042 | 312013.9375 | 133157.6562 | 0 | 99493.7734 | 0 | 25322.7578 | 0 | 0 | 54039.6836 | 0 | 0 | 0 | 0 | 11073.7216 | 110.3944 | 8676.9024 | 2286.4229 | 1483.5428 | 1637.2334 | -2823.1543 | 0 | 0 | 0 | 0 | 1483.5428 | 79362.4414 | 615.8525
EPr-w02-v14-PVAV_Std | EPr | CZ02 | 14 | PVAV_Std | 1.6302 | 314608.6562 | 133157.6562 | 0 | 99493.7734 | 239.0436 | 37487.2422 | 0 | 526.5968 | 43704.2227 | 0 | 0 | 0 | 0 | 11432.192 | 110.3944 | 9034.5235 | 2287.271 | 1539.4395 | 1677.5636 | -1205.5614 | 0 | 0 | 0 | 0 | 1539.4395 | 81957.1053 | 635.9871
EPr-w02-v14-PVAV_Hi | EPr | CZ02 | 14 | PVAV_Hi | 1.6302 | 304967.3438 | 133157.6562 | 0 | 99493.7734 | 463.4263 | 28973.9141 | 0 | 555.634 | 42322.8203 | 0 | 0 | 0 | 0 | 10837.769 | 110.3944 | 8440.009 | 2287.3648 | 1405.1715 | 1660.4471 | -1169.447 | 0 | 0 | 0 | 0 | 1405.1715 | 72315.7947 | 561.1706
EPr-w02-v14-VRF_HP_OAU0 | EPr | CZ02 | 14 | VRF_HP_OAU0 | 1.6302 | 368148.75 | 133157.6562 | 0 | 99493.7734 | 52232.7227 | 32158.4219 | 0 | 0 | 51106.2969 | 0 | 0 | 0 | 0 | 2396.4064 | 110.3944 | 0 | 2286.0117 | 1051.4601 | 1400.6188 | -1464.0166 | 0 | 0 | 0 | 0 | 1051.4601 | 135497.4414 | 1051.4601
EPr-w02-v14-VRF_HP_OAU1 | EPr | CZ02 | 14 | VRF_HP_OAU1 | 1.6302 | 359583.2188 | 133157.6562 | 0 | 99493.7734 | 47425.1328 | 28400.4082 | 0 | 0 | 51106.2969 | 0 | 0 | 0 | 0 | 2396.4064 | 110.3944 | 0 | 2286.0117 | 984.9911 | 1400.6188 | -1464.0166 | 0 | 0 | 0 | 0 | 984.9911 | 126931.8379 | 984.9911
EPr-w02-v14-VRF_HP_OAU2 | EPr | CZ02 | 14 | VRF_HP_OAU2 | 1.6302 | 352132.6562 | 133157.6562 | 0 | 99493.7734 | 43113.1797 | 25261.8516 | 0 | 0 | 51106.2969 | 0 | 0 | 0 | 0 | 2396.4064 | 110.3944 | 0 | 2286.0117 | 927.1751 | 1400.6188 | -1464.0166 | 0 | 0 | 0 | 0 | 927.1751 | 119481.3281 | 927.1751
EPr-w02-v14-VRF_HR_OAU0 | EPr | CZ02 | 14 | VRF_HR_OAU0 | 1.6302 | 357226.875 | 133157.6562 | 0 | 99493.7734 | 44956.6914 | 28597.5898 | 0 | 0 | 51021.0586 | 0 | 0 | 0 | 0 | 2396.3986 | 110.3944 | 0 | 2286.0043 | 966.7046 | 1385.8632 | -1448.4897 | 0.19106 | 0 | 0 | 5 | 966.7046 | 124575.3398 | 966.7046
EPr-w02-v14-VRF_HR_OAU1 | EPr | CZ02 | 14 | VRF_HR_OAU1 | 1.6302 | 349664.8438 | 133157.6562 | 0 | 99493.7734 | 40662.0781 | 25330.2402 | 0 | 0 | 51021.0586 | 0 | 0 | 0 | 0 | 2396.3986 | 110.3944 | 0 | 2286.0043 | 908.0238 | 1385.8632 | -1448.4897 | 0.19106 | 0 | 0 | 5 | 908.0238 | 117013.377 | 908.0238
EPr-w02-v14-VRF_HR_OAU2 | EPr | CZ02 | 14 | VRF_HR_OAU2 | 1.6302 | 343008.3125 | 133157.6562 | 0 | 99493.7734 | 36819.9766 | 22515.8984 | 0 | 0 | 51021.0586 | 0 | 0 | 0 | 0 | 2396.3986 | 110.3944 | 0 | 2286.0043 | 856.3698 | 1385.8632 | -1448.4897 | 0.19106 | 0 | 0 | 5 | 856.3698 | 110356.9336 | 856.3698
Htl-w02-v14-FPFC_1 | Htl | CZ02 | 14 | FPFC_1 | 669.7245 | 3623069.5 | 566447.625 | 0 | 1692748 | 11112.9756 | 538046.3125 | 8381.1807 | 256224.8125 | 550107.9375 | 0 | 0 | 0 | 0 | 183934.0339 | 0 | 143186.4525 | 40747.584 | 24837.2635 | 8444.0977 | -16164.6748 | 0.011414 | 0 | 1 | 0 | 24837.2635 | 1355492.0381 | 10518.6182
Htl-w02-v14-FPFC_2 | Htl | CZ02 | 14 | FPFC_2 | 622.5062 | 3494826.75 | 566447.625 | 0 | 1692748 | 26550.5664 | 381990.4688 | 19470.543 | 256212.8906 | 551406.0625 | 0 | 0 | 0 | 0 | 156984.832 | 0 | 116237.1584 | 40747.6403 | 21061.1173 | 8444.0977 | -16164.6748 | 0.0799 | 0 | 1 | 6 | 21061.1173 | 1216159.9883 | 9437.4015
Htl-w02-v14-VRF_HP_OAU0 | Htl | CZ02 | 14 | VRF_HP_OAU0 | 845.901 | 4052447.5 | 566447.625 | 0 | 1692748 | 917263.75 | 429441.5938 | 0 | 1121.6216 | 445424.0938 | 0 | 0 | 0 | 0 | 40747.8477 | 0 | 0 | 40747.8477 | 13915.6282 | 7407.1011 | -7701.6753 | 0.17121 | 0 | 15 | 0 | 13915.6282 | 1793251.0591 | 13915.6282
Htl-w02-v14-VRF_HP_OAU1 | Htl | CZ02 | 14 | VRF_HP_OAU1 | 775.3184 | 3891685.5 | 566447.625 | 0 | 1692748 | 820307.5625 | 365635.9375 | 0 | 1121.6216 | 445424.0938 | 0 | 0 | 0 | 0 | 40747.8477 | 0 | 0 | 40747.8477 | 12668.1163 | 7407.0991 | -7701.6738 | 0.17121 | 0 | 15 | 0 | 12668.1163 | 1632489.2153 | 12668.1163
Htl-w02-v14-VRF_HP_OAU2 | Htl | CZ02 | 14 | VRF_HP_OAU2 | 720.9396 | 3763636.75 | 566447.625 | 0 | 1692748 | 739442 | 318452.3125 | 0 | 1121.6216 | 445424.0938 | 0 | 0 | 0 | 0 | 40747.8477 | 0 | 0 | 40747.8477 | 11674.4546 | 7407.0972 | -7701.6714 | 0.17121 | 0 | 15 | 0 | 11674.4546 | 1504440.0278 | 11674.4546
Htl-w02-v14-VRF_HR_OAU0 | Htl | CZ02 | 14 | VRF_HR_OAU0 | 827.0341 | 3926173.25 | 566447.625 | 0 | 1692748 | 816720.625 | 404124.0625 | 0 | 1121.6216 | 445009.8125 | 0 | 0 | 0 | 0 | 40747.8195 | 0 | 0 | 40747.8195 | 12935.7347 | 7372.2271 | -7665.1572 | 1.3583 | 0 | 105 | 14 | 12935.7347 | 1666976.1216 | 12935.7347
Htl-w02-v14-VRF_HR_OAU1 | Htl | CZ02 | 14 | VRF_HR_OAU1 | 756.2947 | 3776112.5 | 566447.625 | 0 | 1692748 | 727398.3125 | 343473.0938 | 0 | 1121.6216 | 444922.9062 | 0 | 0 | 0 | 0 | 40747.8246 | 0 | 0 | 40747.8246 | 11771.2676 | 7363.8691 | -7656.3994 | 1.3811 | 0 | 107 | 14 | 11771.2676 | 1516915.9341 | 11771.2676
Htl-w02-v14-VRF_HR_OAU2 | Htl | CZ02 | 14 | VRF_HR_OAU2 | 704.3146 | 3656588.25 | 566447.625 | 0 | 1692748 | 652587.5 | 298894.1875 | 0 | 1121.6216 | 444788.9688 | 0 | 0 | 0 | 0 | 40747.8298 | 0 | 0 | 40747.8298 | 10843.7641 | 7351.0327 | -7642.9453 | 1.3697 | 0 | 106 | 14 | 10843.7641 | 1397392.2778 | 10843.7641
OfS-w03-v14-AC_S1Std | OfS | CZ03 | 14 | AC_S1Std | 32.3553 | 93942.0703 | 31593.9805 | 0 | 50648.0078 | 0 | 4107.9146 | 0 | 0 | 7592.2256 | 0 | 0 | 0 | 0 | 349.4896 | 0 | 163.4544 | 186.0352 | 107.1385 | 208.6171 | -313.1403 | 0 | 0 | 0 | 0 | 107.1385 | 11700.1401 | 90.7931
OfS-w03-v14-AC_S0Std | OfS | CZ03 | 14 | AC_S0Std | 32.3545 | 98011.1016 | 31593.9805 | 0 | 50648.0078 | 0 | 8177.0381 | 0 | 0 | 7592.2056 | 0 | 0 | 0 | 0 | 349.3181 | 0 | 163.2842 | 186.0339 | 138.6978 | 208.754 | -313.1389 | 0 | 0 | 0 | 0 | 138.6978 | 15769.2437 | 122.3693
OfS-w03-v14-AC_SHi | OfS | CZ03 | 14 | AC_SHi | 29.671 | 89553.7969 | 31593.9805 | 0 | 50648.0078 | 0 | 3235.094 | 0 | 0 | 4076.791 | 0 | 0 | 0 | 0 | 376.3343 | 0 | 190.2383 | 186.096 | 75.7641 | 206.0651 | -294.8698 | 0 | 0 | 0 | 0 | 75.7641 | 7311.885 | 56.7402
OfS-w03-v14-AC_EStd | OfS | CZ03 | 14 | AC_EStd | 33.3169 | 92920.6875 | 31593.9805 | 0 | 50648.0078 | 0 | 4359.0581 | 0 | 0 | 6319.729 | 0 | 0 | 0 | 0 | 362.948 | 0 | 176.8689 | 186.0791 | 100.5543 | 207.3422 | -291.7095 | 0 | 0 | 0 | 0 | 100.5543 | 10678.7871 | 82.8674
OfS-w03-v14-AC_EHi | OfS | CZ03 | 14 | AC_EHi | 31.4432 | 92162.7109 | 31593.9805 | 0 | 50648.0078 | 0 | 3601.0642 | 0 | 0 | 6319.729 | 0 | 0 | 0 | 0 | 362.948 | 0 | 176.8689 | 186.0791 | 94.6722 | 207.3422 | -291.7095 | 0 | 0 | 0 | 0 | 94.6722 | 9920.7932 | 76.9854
OfS-w03-v14-PVAV_Std | OfS | CZ03 | 14 | PVAV_Std | 35.6252 | 94478.0625 | 31593.9805 | 0 | 50648.0078 | 17.9512 | 8102.2354 | 0 | 195.3267 | 3920.6047 | 0 | 0 | 0 | 0 | 431.6144 | 0 | 245.7036 | 185.9107 | 119.5226 | 0 | 0 | 0 | 0 | 0 | 0 | 119.5226 | 12236.118 | 94.9523
OfS-w03-v14-PVAV_Hi | OfS | CZ03 | 14 | PVAV_Hi | 32.4617 | 92586.9844 | 31593.9805 | 0 | 50648.0078 | 34.0179 | 6178.3901 | 0 | 195.6369 | 3936.9929 | 0 | 0 | 0 | 0 | 350.476 | 0 | 164.5615 | 185.9144 | 96.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 96.7336 | 10345.0378 | 80.2775
OfS-w03-v14-VRF_HP_OAU0 | OfS | CZ03 | 14 | VRF_HP_OAU0 | 31.2316 | 96118.1172 | 31593.9805 | 0 | 50648.0078 | 1509.5461 | 7968.5444 | 0 | 0 | 4398.1299 | 0 | 0 | 0 | 0 | 186.0483 | 0 | 0 | 186.0483 | 107.6795 | 227.3238 | -237.9122 | 0 | 0 | 0 | 0 | 107.6795 | 13876.2205 | 107.6795
OfS-w03-v14-VRF_HP_OAU1 | OfS | CZ03 | 14 | VRF_HP_OAU1 | 30.1333 | 95048.7266 | 31593.9805 | 0 | 50648.0078 | 1366.9429 | 7041.7437 | 0 | 0 | 4398.1299 | 0 | 0 | 0 | 0 | 186.0483 | 0 | 0 | 186.0483 | 99.3809 | 227.3238 | -237.9122 | 0 | 0 | 0 | 0 | 99.3809 | 12806.8164 | 99.3809
OfS-w03-v14-VRF_HP_OAU2 | OfS | CZ03 | 14 | VRF_HP_OAU2 | 29.1765 | 94147.6797 | 31593.9805 | 0 | 50648.0078 | 1243.7725 | 6263.8657 | 0 | 0 | 4398.1299 | 0 | 0 | 0 | 0 | 186.0483 | 0 | 0 | 186.0483 | 92.3888 | 227.3238 | -237.9122 | 0 | 0 | 0 | 0 | 92.3888 | 11905.7681 | 92.3888
OfS-w03-v14-VRF_HR_OAU0 | OfS | CZ03 | 14 | VRF_HR_OAU0 | 30.7528 | 95255.75 | 31593.9805 | 0 | 50648.0078 | 1222.464 | 7393.1016 | 0 | 0 | 4398.2891 | 0 | 0 | 0 | 0 | 186.0378 | 0 | 0 | 186.0378 | 100.9875 | 226.9061 | -237.4857 | 0 | 0 | 0 | 0 | 100.9875 | 13013.8546 | 100.9875
OfS-w03-v14-VRF_HR_OAU1 | OfS | CZ03 | 14 | VRF_HR_OAU1 | 29.7434 | 94306.2656 | 31593.9805 | 0 | 50648.0078 | 1103.514 | 6562.5649 | 0 | 0 | 4398.2891 | 0 | 0 | 0 | 0 | 186.0378 | 0 | 0 | 186.0378 | 93.6195 | 226.9061 | -237.4857 | 0 | 0 | 0 | 0 | 93.6195 | 12064.368 | 93.6195
OfS-w03-v14-VRF_HR_OAU2 | OfS | CZ03 | 14 | VRF_HR_OAU2 | 28.8972 | 93503.3828 | 31593.9805 | 0 | 50648.0078 | 998.74 | 5864.4561 | 0 | 0 | 4398.2891 | 0 | 0 | 0 | 0 | 186.0378 | 0 | 0 | 186.0378 | 87.3891 | 226.9061 | -237.4857 | 0 | 0 | 0 | 0 | 87.3891 | 11261.4851 | 87.3891
OfL-w03-v14-FPFC_1 | OfL | CZ03 | 14 | FPFC_1 | 475.8599 | 1710957.375 | 500422.4062 | 0 | 883691.5 | 263.099 | 190859.8438 | 3305.7102 | 62721.0195 | 69694.9688 | 0 | 0 | 0 | 0 | 6479.9174 | 0 | 3364.6726 | 3115.2451 | 2847.1294 | 3416.4893 | -6930.6201 | 0 | 0 | 0 | 0 | 2847.1294 | 323538.931 | 2510.6621
OfL-w03-v14-FPFC_2 | OfL | CZ03 | 14 | FPFC_2 | 452.936 | 1662125.75 | 500422.4062 | 0 | 883691.5 | 555.1203 | 139105.0625 | 6216.957 | 62528.1641 | 69608.3438 | 0 | 0 | 0 | 0 | 4890.433 | 0 | 1775.1571 | 3115.2755 | 2286.658 | 3416.4893 | -6930.6201 | 0 | 0 | 0 | 0 | 2286.658 | 271796.6906 | 2109.1423
OfL-w03-v14-VRF_HP_OAU0 | OfL | CZ03 | 14 | VRF_HP_OAU0 | 509.9232 | 1651887 | 500422.4062 | 0 | 883691.5 | 5641.9932 | 180693.5469 | 0 | 213.4769 | 81225.3125 | 0 | 0 | 0 | 0 | 3114.8742 | 0 | 0 | 3114.8742 | 2077.9288 | 4135.0625 | -4327.3262 | 0 | 0 | 0 | 0 | 2077.9288 | 267774.3294 | 2077.9288
OfL-w03-v14-VRF_HP_OAU1 | OfL | CZ03 | 14 | VRF_HP_OAU1 | 478.9447 | 1619044.375 | 500422.4062 | 0 | 883691.5 | 4835.9756 | 148657.3125 | 0 | 213.4769 | 81225.3125 | 0 | 0 | 0 | 0 | 3114.8742 | 0 | 0 | 3114.8742 | 1823.0729 | 4135.0625 | -4327.3262 | 0 | 0 | 0 | 0 | 1823.0729 | 234932.0775 | 1823.0729
OfL-w03-v14-VRF_HP_OAU2 | OfL | CZ03 | 14 | VRF_HP_OAU2 | 461.8945 | 1600921.125 | 500422.4062 | 0 | 883691.5 | 4364.415 | 131005.7266 | 0 | 213.4769 | 81225.3125 | 0 | 0 | 0 | 0 | 3114.8742 | 0 | 0 | 3114.8742 | 1682.4373 | 4135.0625 | -4327.3262 | 0 | 0 | 0 | 0 | 1682.4373 | 216808.931 | 1682.4373
OfL-w03-v14-VRF_HR_OAU0 | OfL | CZ03 | 14 | VRF_HR_OAU0 | 508.9862 | 1640503.5 | 500422.4062 | 0 | 883691.5 | 4546.6577 | 170099.5312 | 0 | 213.4769 | 81531.4297 | 0 | 0 | 0 | 0 | 3114.8589 | 0 | 0 | 3114.8589 | 1989.5949 | 4145.0288 | -4337.3857 | 0 | 0 | 0 | 0 | 1989.5949 | 256391.0955 | 1989.5949
OfL-w03-v14-VRF_HR_OAU1 | OfL | CZ03 | 14 | VRF_HR_OAU1 | 478.1314 | 1609612 | 500422.4062 | 0 | 883691.5 | 3855.1104 | 139899.7812 | 0 | 213.4769 | 81531.4297 | 0 | 0 | 0 | 0 | 3114.8589 | 0 | 0 | 3114.8589 | 1749.8784 | 4145.0288 | -4337.3857 | 0 | 0 | 0 | 0 | 1749.8784 | 225499.7982 | 1749.8784
OfL-w03-v14-VRF_HR_OAU2 | OfL | CZ03 | 14 | VRF_HR_OAU2 | 461.149 | 1592671.625 | 500422.4062 | 0 | 883691.5 | 3460.7725 | 123353.8906 | 0 | 213.4769 | 81531.4297 | 0 | 0 | 0 | 0 | 3114.8589 | 0 | 0 | 3114.8589 | 1618.4223 | 4145.0288 | -4337.3857 | 0 | 0 | 0 | 0 | 1618.4223 | 208559.5696 | 1618.4223
EPr-w03-v14-AC_S1Std | EPr | CZ03 | 14 | AC_S1Std | 1.6302 | 294322.125 | 133157.6562 | 0 | 99493.7734 | 0 | 13207.4375 | 0 | 0 | 48463.6289 | 0 | 0 | 0 | 0 | 10121.0054 | 110.3944 | 7721.8221 | 2288.7904 | 1250.7497 | 1282.7905 | -2709.5364 | 0 | 0 | 0 | 0 | 1250.7497 | 61671.0664 | 478.5675
EPr-w03-v14-AC_S0Std | EPr | CZ03 | 14 | AC_S0Std | 1.6302 | 297865.1875 | 133157.6562 | 0 | 99493.7734 | 0 | 16750.3516 | 0 | 0 | 48463.6211 | 0 | 0 | 0 | 0 | 10120.8742 | 110.3944 | 7721.6902 | 2288.7901 | 1278.2295 | 1282.7899 | -2709.5349 | 0 | 0 | 0 | 0 | 1278.2295 | 65213.9727 | 506.0604
EPr-w03-v14-AC_SHi | EPr | CZ03 | 14 | AC_SHi | 1.6302 | 279018.0938 | 133157.6562 | 0 | 99493.7734 | 0 | 10499.5625 | 0 | 0 | 35867.6836 | 0 | 0 | 0 | 0 | 10338.0256 | 110.3944 | 7938.6842 | 2288.9467 | 1153.6782 | 1258.801 | -2504.3184 | 0 | 0 | 0 | 0 | 1153.6782 | 46367.2461 | 359.8098
EPr-w03-v14-AC_EStd | EPr | CZ03 | 14 | AC_EStd | 1.6302 | 293975.0938 | 133157.6562 | 0 | 99493.7734 | 0 | 14319.2822 | 0 | 0 | 47004.8398 | 0 | 0 | 0 | 0 | 10051.9251 | 110.3944 | 7652.6093 | 2288.9227 | 1241.1361 | 1292.2942 | -2494.196 | 0 | 0 | 0 | 0 | 1241.1361 | 61324.1221 | 475.8752
EPr-w03-v14-AC_EHi | EPr | CZ03 | 14 | AC_EHi | 1.6302 | 291484.9375 | 133157.6562 | 0 | 99493.7734 | 0 | 11829.3115 | 0 | 0 | 47004.8398 | 0 | 0 | 0 | 0 | 10051.9251 | 110.3944 | 7652.6093 | 2288.9227 | 1221.8139 | 1292.2942 | -2494.196 | 0 | 0 | 0 | 0 | 1221.8139 | 58834.1514 | 456.553
EPr-w03-v14-PVAV_Std | EPr | CZ03 | 14 | PVAV_Std | 1.6302 | 296749.5625 | 133157.6562 | 0 | 99493.7734 | 201.9597 | 22095.4805 | 0 | 391.7003 | 41408.9336 | 0 | 0 | 0 | 0 | 10471.6288 | 110.3944 | 8071.6461 | 2289.5894 | 1304.5657 | 1351.0457 | -1001.2148 | 0 | 0 | 0 | 0 | 1304.5657 | 64098.0741 | 497.4011
EPr-w03-v14-PVAV_Hi | EPr | CZ03 | 14 | PVAV_Hi | 1.6302 | 291104.9688 | 133157.6562 | 0 | 99493.7734 | 405.0606 | 17144.5254 | 0 | 392.6192 | 40511.8125 | 0 | 0 | 0 | 0 | 10009.3658 | 110.3944 | 7609.3088 | 2289.6626 | 1214.5341 | 1338.619 | -997.6669 | 0 | 0 | 0 | 0 | 1214.5341 | 58454.0177 | 453.6032
EPr-w03-v14-VRF_HP_OAU0 | EPr | CZ03 | 14 | VRF_HP_OAU0 | 1.6302 | 339935.9375 | 133157.6562 | 0 | 99493.7734 | 41855.4375 | 15668.0166 | 0 | 0 | 49761.0273 | 0 | 0 | 0 | 0 | 2398.9216 | 110.3944 | 0 | 2288.5272 | 832.5276 | 1206.2437 | -1262.2875 | 0 | 0 | 0 | 0 | 832.5276 | 107284.4814 | 832.5276
EPr-w03-v14-VRF_HP_OAU1 | EPr | CZ03 | 14 | VRF_HP_OAU1 | 1.6302 | 334130.5 | 133157.6562 | 0 | 99493.7734 | 37858.4688 | 13859.5947 | 0 | 0 | 49761.0273 | 0 | 0 | 0 | 0 | 2398.9216 | 110.3944 | 0 | 2288.5272 | 787.4777 | 1206.2437 | -1262.2875 | 0 | 0 | 0 | 0 | 787.4777 | 101479.0908 | 787.4777
EPr-w03-v14-VRF_HP_OAU2 | EPr | CZ03 | 14 | VRF_HP_OAU2 | 1.6302 | 329078.1562 | 133157.6562 | 0 | 99493.7734 | 34324.8047 | 12341.124 | 0 | 0 | 49761.0273 | 0 | 0 | 0 | 0 | 2398.9216 | 110.3944 | 0 | 2288.5272 | 748.2732 | 1206.2437 | -1262.2875 | 0 | 0 | 0 | 0 | 748.2732 | 96426.9561 | 748.2732
EPr-w03-v14-VRF_HR_OAU0 | EPr | CZ03 | 14 | VRF_HR_OAU0 | 1.6302 | 332385.5625 | 133157.6562 | 0 | 99493.7734 | 35721.8516 | 14280.0957 | 0 | 0 | 49732.2656 | 0 | 0 | 0 | 0 | 2398.9182 | 110.3944 | 0 | 2288.5232 | 773.9375 | 1199.9064 | -1255.447 | 0.038212 | 0 | 0 | 1 | 773.9375 | 99734.2129 | 773.9375
EPr-w03-v14-VRF_HR_OAU1 | EPr | CZ03 | 14 | VRF_HR_OAU1 | 1.6302 | 327171.5312 | 133157.6562 | 0 | 99493.7734 | 32141.9277 | 12646.0967 | 0 | 0 | 49732.2656 | 0 | 0 | 0 | 0 | 2398.9182 | 110.3944 | 0 | 2288.5232 | 733.4775 | 1199.9064 | -1255.447 | 0.038212 | 0 | 0 | 1 | 733.4775 | 94520.29 | 733.4775
EPr-w03-v14-VRF_HR_OAU2 | EPr | CZ03 | 14 | VRF_HR_OAU2 | 1.6302 | 322717.4062 | 133157.6562 | 0 | 99493.7734 | 29064.5938 | 11269.5205 | 0 | 0 | 49732.2656 | 0 | 0 | 0 | 0 | 2398.9182 | 110.3944 | 0 | 2288.5232 | 698.9151 | 1199.9064 | -1255.447 | 0.038212 | 0 | 0 | 1 | 698.9151 | 90066.3799 | 698.9151
Htl-w03-v14-FPFC_1 | Htl | CZ03 | 14 | FPFC_1 | 556.67 | 3378867.75 | 566447.625 | 0 | 1692748 | 9766.2666 | 403554.3125 | 6088.6646 | 217912.2031 | 482350.2188 | 0 | 0 | 0 | 0 | 166796.4723 | 0 | 125886.2592 | 40910.1824 | 21230.03 | 7150.8711 | -13112.3213 | 0 | 0 | 0 | 0 | 21230.03 | 1113583.001 | 8641.4041
Htl-w03-v14-FPFC_2 | Htl | CZ03 | 14 | FPFC_2 | 520.6327 | 3280103 | 566447.625 | 0 | 1692748 | 23865.0059 | 283534.2188 | 12754.915 | 217973.0938 | 482779.7812 | 0 | 0 | 0 | 0 | 143767.2653 | 0 | 102857.0522 | 40910.1824 | 18108.9655 | 7150.8711 | -13112.3213 | 0.057071 | 0 | 0 | 5 | 18108.9655 | 1008152.0996 | 7823.2603
Htl-w03-v14-VRF_HP_OAU0 | Htl | CZ03 | 14 | VRF_HP_OAU0 | 590.1246 | 3664908.5 | 566447.625 | 0 | 1692748 | 734412.9375 | 244332.875 | 0 | 1121.6216 | 425844.6562 | 0 | 0 | 0 | 0 | 40910.4666 | 0 | 0 | 40910.4666 | 10908.3258 | 6343.4697 | -6596.0454 | 0 | 0 | 0 | 0 | 10908.3258 | 1405712.0903 | 10908.3258
Htl-w03-v14-VRF_HP_OAU1 | Htl | CZ03 | 14 | VRF_HP_OAU1 | 553.4656 | 3549787.25 | 566447.625 | 0 | 1692748 | 656357.125 | 207267.5 | 0 | 1121.6216 | 425844.625 | 0 | 0 | 0 | 0 | 40910.4666 | 0 | 0 | 40910.4666 | 10014.9852 | 6343.4629 | -6596.0381 | 0 | 0 | 0 | 0 | 10014.9852 | 1290590.8716 | 10014.9852
Htl-w03-v14-VRF_HP_OAU2 | Htl | CZ03 | 14 | VRF_HP_OAU2 | 524.8334 | 3457756 | 566447.625 | 0 | 1692748 | 591403.5625 | 180190.2656 | 0 | 1121.6216 | 425844.75 | 0 | 0 | 0 | 0 | 40910.4666 | 0 | 0 | 40910.4666 | 9300.8271 | 6343.459 | -6596.0337 | 0 | 0 | 0 | 0 | 9300.8271 | 1198560.1997 | 9300.8271
Htl-w03-v14-VRF_HR_OAU0 | Htl | CZ03 | 14 | VRF_HR_OAU0 | 570.4153 | 3563423.5 | 566447.625 | 0 | 1692748 | 650624.3125 | 227801.2344 | 0 | 1121.6216 | 424680.0938 | 0 | 0 | 0 | 0 | 40910.4794 | 0 | 0 | 40910.4794 | 10120.8036 | 6291.3896 | -6541.4814 | 0.86748 | 0 | 75 | 1 | 10120.8036 | 1304227.2622 | 10120.8036
Htl-w03-v14-VRF_HR_OAU1 | Htl | CZ03 | 14 | VRF_HR_OAU1 | 537.048 | 3454070.25 | 566447.625 | 0 | 1692748 | 576450.25 | 192600.3594 | 0 | 1121.6216 | 424701.75 | 0 | 0 | 0 | 0 | 40910.4794 | 0 | 0 | 40910.4794 | 9272.2221 | 6291.3853 | -6541.4775 | 0.86748 | 0 | 75 | 1 | 9272.2221 | 1194873.981 | 9272.2221
Htl-w03-v14-VRF_HR_OAU2 | Htl | CZ03 | 14 | VRF_HR_OAU2 | 512.4104 | 3368493 | 566447.625 | 0 | 1692748 | 516348.125 | 167125.3594 | 0 | 1121.6216 | 424701.8125 | 0 | 0 | 0 | 0 | 40910.4794 | 0 | 0 | 40910.4794 | 8608.1441 | 6291.3789 | -6541.4707 | 0.86748 | 0 | 75 | 1 | 8608.1441 | 1109296.9185 | 8608.1441
OfS-w04-v14-AC_S1Std | OfS | CZ04 | 14 | AC_S1Std | 37.3553 | 99678.2969 | 31593.9805 | 0 | 50648.0078 | 0 | 9073.499 | 0 | 0 | 8362.9443 | 0 | 0 | 0 | 0 | 303.7483 | 0 | 123.1209 | 180.6274 | 147.6189 | 235.9091 | -362.9149 | 0 | 0 | 0 | 0 | 147.6189 | 17436.4434 | 135.3068
OfS-w04-v14-AC_S0Std | OfS | CZ04 | 14 | AC_S0Std | 37.3598 | 103473.2188 | 31593.9805 | 0 | 50648.0078 | 0 | 12868.8398 | 0 | 0 | 8362.4961 | 0 | 0 | 0 | 0 | 303.5831 | 0 | 122.957 | 180.6262 | 177.0509 | 236.1529 | -362.9019 | 0 | 0 | 0 | 0 | 177.0509 | 21231.3359 | 164.7552
OfS-w04-v14-AC_SHi | OfS | CZ04 | 14 | AC_SHi | 34.098 | 93969.2188 | 31593.9805 | 0 | 50648.0078 | 0 | 7238.832 | 0 | 0 | 4488.4839 | 0 | 0 | 0 | 0 | 323.2832 | 0 | 142.5916 | 180.6917 | 105.2631 | 235.4952 | -326.1501 | 0 | 0 | 0 | 0 | 105.2631 | 11727.3159 | 91.004
OfS-w04-v14-AC_EStd | OfS | CZ04 | 14 | AC_EStd | 39.1584 | 99004.7656 | 31593.9805 | 0 | 50648.0078 | 0 | 9728.8281 | 0 | 0 | 7034.0664 | 0 | 0 | 0 | 0 | 312.5364 | 0 | 131.8623 | 180.6741 | 143.2663 | 234.8203 | -322.7398 | 0 | 0 | 0 | 0 | 143.2663 | 16762.8945 | 130.0801
OfS-w04-v14-AC_EHi | OfS | CZ04 | 14 | AC_EHi | 36.3825 | 97313.0547 | 31593.9805 | 0 | 50648.0078 | 0 | 8037.0884 | 0 | 0 | 7034.0664 | 0 | 0 | 0 | 0 | 312.5364 | 0 | 131.8623 | 180.6741 | 130.1384 | 234.8203 | -322.7398 | 0 | 0 | 0 | 0 | 130.1384 | 15071.1548 | 116.9522
OfS-w04-v14-PVAV_Std | OfS | CZ04 | 14 | PVAV_Std | 41.8603 | 101352.1328 | 31593.9805 | 0 | 50648.0078 | 15.7223 | 14568.8223 | 0 | 215.9318 | 4309.7305 | 0 | 0 | 0 | 0 | 395.2324 | 0 | 214.5718 | 180.6606 | 169.7524 | 0 | 0 | 0 | 0 | 0 | 0 | 169.7524 | 19110.2069 | 148.2952
OfS-w04-v14-PVAV_Hi | OfS | CZ04 | 14 | PVAV_Hi | 37.2385 | 97880.5078 | 31593.9805 | 0 | 50648.0078 | 30.8505 | 11086.0137 | 0 | 216.8643 | 4304.8643 | 0 | 0 | 0 | 0 | 320.7389 | 0 | 140.0755 | 180.6634 | 135.363 | 0 | 0 | 0 | 0 | 0 | 0 | 135.363 | 15638.5928 | 121.3555
OfS-w04-v14-VRF_HP_OAU0 | OfS | CZ04 | 14 | VRF_HP_OAU0 | 37.1539 | 100640.4141 | 31593.9805 | 0 | 50648.0078 | 1236.071 | 12599.5205 | 0 | 0 | 4562.9531 | 0 | 0 | 0 | 0 | 180.6242 | 0 | 0 | 180.6242 | 142.7727 | 240.5686 | -250.9182 | 0 | 0 | 0 | 0 | 142.7727 | 18398.5447 | 142.7727
OfS-w04-v14-VRF_HP_OAU1 | OfS | CZ04 | 14 | VRF_HP_OAU1 | 35.3165 | 99057.7188 | 31593.9805 | 0 | 50648.0078 | 1119.3917 | 11133.4814 | 0 | 0 | 4562.9531 | 0 | 0 | 0 | 0 | 180.6242 | 0 | 0 | 180.6242 | 130.4908 | 240.5686 | -250.9182 | 0 | 0 | 0 | 0 | 130.4908 | 16815.8263 | 130.4908
OfS-w04-v14-VRF_HP_OAU2 | OfS | CZ04 | 14 | VRF_HP_OAU2 | 33.7657 | 97719.0234 | 31593.9805 | 0 | 50648.0078 | 1017.7495 | 9896.4219 | 0 | 0 | 4562.9531 | 0 | 0 | 0 | 0 | 180.6242 | 0 | 0 | 180.6242 | 120.1025 | 240.5686 | -250.9182 | 0 | 0 | 0 | 0 | 120.1025 | 15477.1245 | 120.1025
OfS-w04-v14-VRF_HR_OAU0 | OfS | CZ04 | 14 | VRF_HR_OAU0 | 36.5883 | 99637.6719 | 31593.9805 | 0 | 50648.0078 | 1005.204 | 11829.1094 | 0 | 0 | 4561.4644 | 0 | 0 | 0 | 0 | 180.6088 | 0 | 0 | 180.6088 | 134.9912 | 239.221 | -249.5032 | 0 | 0 | 0 | 0 | 134.9912 | 17395.7778 | 134.9912
OfS-w04-v14-VRF_HR_OAU1 | OfS | CZ04 | 14 | VRF_HR_OAU1 | 34.7484 | 98161.7109 | 31593.9805 | 0 | 50648.0078 | 905.8532 | 10452.4912 | 0 | 0 | 4561.4644 | 0 | 0 | 0 | 0 | 180.6088 | 0 | 0 | 180.6088 | 123.5377 | 239.221 | -249.5032 | 0 | 0 | 0 | 0 | 123.5377 | 15919.8088 | 123.5377
OfS-w04-v14-VRF_HR_OAU2 | OfS | CZ04 | 14 | VRF_HR_OAU2 | 33.236 | 96923.1719 | 31593.9805 | 0 | 50648.0078 | 821.1799 | 9298.6074 | 0 | 0 | 4561.4644 | 0 | 0 | 0 | 0 | 180.6088 | 0 | 0 | 180.6088 | 113.9265 | 239.221 | -249.5032 | 0 | 0 | 0 | 0 | 113.9265 | 14681.2517 | 113.9265
OfL-w04-v14-FPFC_1 | OfL | CZ04 | 14 | FPFC_1 | 509.7171 | 1774178.25 | 500422.4062 | 0 | 883691.5 | 277.527 | 237051.9375 | 4508.9526 | 75374.1641 | 72852.9375 | 0 | 0 | 0 | 0 | 6566.0474 | 0 | 3547.9661 | 3018.0826 | 3346.7156 | 3784.5603 | -7990.979 | 0 | 0 | 0 | 0 | 3346.7156 | 385556.566 | 2991.919
OfL-w04-v14-FPFC_2 | OfL | CZ04 | 14 | FPFC_2 | 484.3884 | 1715996.5 | 500422.4062 | 0 | 883691.5 | 583.4727 | 174178.1094 | 8965.9688 | 75317.8125 | 72838.7188 | 0 | 0 | 0 | 0 | 4920.8698 | 0 | 1902.7587 | 3018.111 | 2696.1204 | 3784.5603 | -7990.979 | 0 | 0 | 0 | 0 | 2696.1204 | 322918.1133 | 2505.8446
OfL-w04-v14-VRF_HP_OAU0 | OfL | CZ04 | 14 | VRF_HP_OAU0 | 617.9565 | 1721443 | 500422.4062 | 0 | 883691.5 | 7030.1963 | 248128.1094 | 0 | 213.4769 | 81959.0078 | 0 | 0 | 0 | 0 | 3017.5926 | 0 | 0 | 3017.5926 | 2617.6869 | 4137.459 | -4317.314 | 0 | 0 | 0 | 0 | 2617.6869 | 337330.7903 | 2617.6869
OfL-w04-v14-VRF_HP_OAU1 | OfL | CZ04 | 14 | VRF_HP_OAU1 | 567.2574 | 1676628.125 | 500422.4062 | 0 | 883691.5 | 6062.6733 | 204280.9062 | 0 | 213.4769 | 81959.0078 | 0 | 0 | 0 | 0 | 3017.5926 | 0 | 0 | 3017.5926 | 2269.9247 | 4137.459 | -4317.314 | 0 | 0 | 0 | 0 | 2269.9247 | 292516.0643 | 2269.9247
OfL-w04-v14-VRF_HP_OAU2 | OfL | CZ04 | 14 | VRF_HP_OAU2 | 544.3799 | 1652924.625 | 500422.4062 | 0 | 883691.5 | 5487.6909 | 181620.8125 | 0 | 213.4769 | 81490.2578 | 0 | 0 | 0 | 0 | 3017.5882 | 0 | 0 | 3017.5882 | 2085.983 | 4094.8596 | -4272.5107 | 0 | 0 | 0 | 0 | 2085.983 | 268812.2381 | 2085.983
OfL-w04-v14-VRF_HR_OAU0 | OfL | CZ04 | 14 | VRF_HR_OAU0 | 624.8077 | 1707524.25 | 500422.4062 | 0 | 883691.5 | 5725.8843 | 234710.7031 | 0 | 213.4769 | 82761.7734 | 0 | 0 | 0 | 0 | 3017.5718 | 0 | 0 | 3017.5718 | 2509.6759 | 4217.4199 | -4398.7437 | 0 | 0 | 0 | 0 | 2509.6759 | 323411.8377 | 2509.6759
OfL-w04-v14-VRF_HR_OAU1 | OfL | CZ04 | 14 | VRF_HR_OAU1 | 567.3309 | 1665430.125 | 500422.4062 | 0 | 883691.5 | 4904.8262 | 193437.5 | 0 | 213.4769 | 82761.7734 | 0 | 0 | 0 | 0 | 3017.5718 | 0 | 0 | 3017.5718 | 2183.0244 | 4217.4199 | -4398.7437 | 0 | 0 | 0 | 0 | 2183.0244 | 281317.5765 | 2183.0244
OfL-w04-v14-VRF_HR_OAU2 | OfL | CZ04 | 14 | VRF_HR_OAU2 | 535.7767 | 1642464.75 | 500422.4062 | 0 | 883691.5 | 4431.8384 | 170945.5469 | 0 | 213.4769 | 82761.7734 | 0 | 0 | 0 | 0 | 3017.5718 | 0 | 0 | 3017.5718 | 2004.8165 | 4217.4199 | -4398.7437 | 0 | 0 | 0 | 0 | 2004.8165 | 258352.6356 | 2004.8165
EPr-w04-v14-AC_S1Std | EPr | CZ04 | 14 | AC_S1Std | 173.8242 | 314668.5 | 133157.6562 | 0 | 99493.7734 | 0 | 31847.582 | 0 | 0 | 50169.6992 | 0 | 0 | 0 | 0 | 8725.111 | 110.3944 | 6391.8611 | 2222.857 | 1275.6402 | 1371.8317 | -3118.5925 | 0.076423 | 0 | 2 | 0 | 1275.6402 | 82017.2812 | 636.4541
EPr-w04-v14-AC_S0Std | EPr | CZ04 | 14 | AC_S0Std | 173.8252 | 318485.2188 | 133157.6562 | 0 | 99493.7734 | 0 | 35663.793 | 0 | 0 | 50170 | 0 | 0 | 0 | 0 | 8724.9766 | 110.3944 | 6391.7248 | 2222.8563 | 1305.2427 | 1371.8402 | -3118.6099 | 0.076423 | 0 | 2 | 0 | 1305.2427 | 85833.793 | 666.0702
EPr-w04-v14-AC_SHi | EPr | CZ04 | 14 | AC_SHi | 154.7164 | 295356.5312 | 133157.6562 | 0 | 99493.7734 | 0 | 25476.9668 | 0 | 0 | 37228.2461 | 0 | 0 | 0 | 0 | 8884.8397 | 110.3944 | 6551.4387 | 2223.0078 | 1141.7363 | 1353.5725 | -2866.9133 | 0.038212 | 0 | 1 | 0 | 1141.7363 | 62705.2129 | 486.5925
EPr-w04-v14-AC_EStd | EPr | CZ04 | 14 | AC_EStd | 187.3276 | 317213.5 | 133157.6562 | 0 | 99493.7734 | 0 | 34785.4375 | 0 | 0 | 49776.707 | 0 | 0 | 0 | 0 | 8647.6077 | 110.3944 | 6314.2317 | 2222.9806 | 1287.6254 | 1401.0236 | -2874.8445 | 0.076423 | 0 | 2 | 0 | 1287.6254 | 84562.1445 | 656.2022
EPr-w04-v14-AC_EHi | EPr | CZ04 | 14 | AC_EHi | 170.9912 | 311164.6875 | 133157.6562 | 0 | 99493.7734 | 0 | 28736.6172 | 0 | 0 | 49776.707 | 0 | 0 | 0 | 0 | 8647.6077 | 110.3944 | 6314.2317 | 2222.9806 | 1240.6866 | 1401.0236 | -2874.8445 | 0.076423 | 0 | 2 | 0 | 1240.6866 | 78513.3242 | 609.2634
EPr-w04-v14-PVAV_Std | EPr | CZ04 | 14 | PVAV_Std | 188.1511 | 319715.625 | 133157.6562 | 0 | 99493.7734 | 178.1589 | 43869.832 | 0 | 414.5262 | 42601.6367 | 0 | 0 | 0 | 0 | 9103.8771 | 110.3944 | 6769.8176 | 2223.6637 | 1352.5996 | 1435.8568 | -1173.1818 | 0.076423 | 0 | 2 | 0 | 1352.5996 | 87064.1538 | 675.6178
EPr-w04-v14-PVAV_Hi | EPr | CZ04 | 14 | PVAV_Hi | 163.979 | 308926.0625 | 133157.6562 | 0 | 99493.7734 | 371.7625 | 33871.4219 | 0 | 422.6262 | 41608.793 | 0 | 0 | 0 | 0 | 8671.4195 | 110.3944 | 6337.2698 | 2223.7558 | 1225.6179 | 1420.6235 | -1162.4734 | 0 | 0 | 0 | 0 | 1225.6179 | 76274.6035 | 591.8909
EPr-w04-v14-VRF_HP_OAU0 | EPr | CZ04 | 14 | VRF_HP_OAU0 | 182.5331 | 354592.1875 | 133157.6562 | 0 | 99493.7734 | 35372.4141 | 36067.9062 | 0 | 0 | 50500.3672 | 0 | 0 | 0 | 0 | 2332.9682 | 110.3944 | 0 | 2222.5742 | 946.2597 | 1308.2451 | -1364.29 | 0 | 0 | 0 | 0 | 946.2597 | 121940.6875 | 946.2597
EPr-w04-v14-VRF_HP_OAU1 | EPr | CZ04 | 14 | VRF_HP_OAU1 | 172.2173 | 347043.4375 | 133157.6562 | 0 | 99493.7734 | 32037.4453 | 31854.248 | 0 | 0 | 50500.3711 | 0 | 0 | 0 | 0 | 2332.9682 | 110.3944 | 0 | 2222.5742 | 887.6824 | 1308.2468 | -1364.2917 | 0 | 0 | 0 | 0 | 887.6824 | 114392.0645 | 887.6824
EPr-w04-v14-VRF_HP_OAU2 | EPr | CZ04 | 14 | VRF_HP_OAU2 | 163.3393 | 340567.4062 | 133157.6562 | 0 | 99493.7734 | 29113.7637 | 28301.8789 | 0 | 0 | 50500.3711 | 0 | 0 | 0 | 0 | 2332.9682 | 110.3944 | 0 | 2222.5742 | 837.4283 | 1308.2468 | -1364.2917 | 0 | 0 | 0 | 0 | 837.4283 | 107916.0137 | 837.4283
EPr-w04-v14-VRF_HR_OAU0 | EPr | CZ04 | 14 | VRF_HR_OAU0 | 174.3795 | 345854.6875 | 133157.6562 | 0 | 99493.7734 | 30338.3867 | 32403.4121 | 0 | 0 | 50461.6055 | 0 | 0 | 0 | 0 | 2332.9602 | 110.3944 | 0 | 2222.5662 | 878.4584 | 1299.5657 | -1355.0792 | 0.076423 | 0 | 0 | 2 | 878.4584 | 113203.4043 | 878.4584
EPr-w04-v14-VRF_HR_OAU1 | EPr | CZ04 | 14 | VRF_HR_OAU1 | 165.2983 | 339109.5312 | 133157.6562 | 0 | 99493.7734 | 27373.7207 | 28622.9336 | 0 | 0 | 50461.6055 | 0 | 0 | 0 | 0 | 2332.9602 | 110.3944 | 0 | 2222.5662 | 826.1161 | 1299.5657 | -1355.0792 | 0.076423 | 0 | 0 | 2 | 826.1161 | 106458.2598 | 826.1161
EPr-w04-v14-VRF_HR_OAU2 | EPr | CZ04 | 14 | VRF_HR_OAU2 | 156.1986 | 333275.8125 | 133157.6562 | 0 | 99493.7734 | 24781.1992 | 25381.7773 | 0 | 0 | 50461.6055 | 0 | 0 | 0 | 0 | 2332.9602 | 110.3944 | 0 | 2222.5662 | 780.8468 | 1299.5657 | -1355.0792 | 0.076423 | 0 | 0 | 2 | 780.8468 | 100624.582 | 780.8468
Htl-w04-v14-FPFC_1 | Htl | CZ04 | 14 | FPFC_1 | 638.3967 | 3604455 | 566447.625 | 0 | 1692748 | 9473.3037 | 559683.5 | 9623.457 | 259276.6875 | 507201.7812 | 0 | 0 | 0 | 0 | 161373.0099 | 0 | 122173.6038 | 39199.4214 | 22581.8901 | 7729.5781 | -15742.083 | 0.011414 | 0 | 1 | 0 | 22581.8901 | 1335635.2725 | 10364.5297
Htl-w04-v14-FPFC_2 | Htl | CZ04 | 14 | FPFC_2 | 594.9582 | 3470811.75 | 566447.625 | 0 | 1692748 | 24496.7969 | 398206.2188 | 21238.0605 | 259497.6094 | 508176.4062 | 0 | 0 | 0 | 0 | 137238.743 | 0 | 98039.337 | 39199.4317 | 19041.2595 | 7729.5781 | -15742.083 | 0.022828 | 0 | 1 | 1 | 19041.2595 | 1190377.0312 | 9237.3258
Htl-w04-v14-VRF_HP_OAU0 | Htl | CZ04 | 14 | VRF_HP_OAU0 | 774.0236 | 3904156.75 | 566447.625 | 0 | 1692748 | 740510.4375 | 462149.1562 | 0 | 1121.6216 | 441179.375 | 0 | 0 | 0 | 0 | 39199.6467 | 0 | 0 | 39199.6467 | 12764.8942 | 7048.8691 | -7311.3452 | 0.22828 | 0 | 20 | 0 | 12764.8942 | 1644960.5903 | 12764.8942
Htl-w04-v14-VRF_HP_OAU1 | Htl | CZ04 | 14 | VRF_HP_OAU1 | 710.2145 | 3762466.25 | 566447.625 | 0 | 1692748 | 665547.9375 | 395420.8438 | 0 | 1121.6216 | 441179.2812 | 0 | 0 | 0 | 0 | 39199.6467 | 0 | 0 | 39199.6467 | 11665.3727 | 7048.8428 | -7311.3174 | 0.22828 | 0 | 20 | 0 | 11665.3727 | 1503269.6841 | 11665.3727
Htl-w04-v14-VRF_HP_OAU2 | Htl | CZ04 | 14 | VRF_HP_OAU2 | 665.2898 | 3649118.5 | 566447.625 | 0 | 1692748 | 601863.0625 | 345757.625 | 0 | 1121.6216 | 441179.25 | 0 | 0 | 0 | 0 | 39199.6467 | 0 | 0 | 39199.6467 | 10785.7913 | 7048.8164 | -7311.29 | 0.22828 | 0 | 20 | 0 | 10785.7913 | 1389921.5591 | 10785.7913
Htl-w04-v14-VRF_HR_OAU0 | Htl | CZ04 | 14 | VRF_HR_OAU0 | 744.9257 | 3807330.25 | 566447.625 | 0 | 1692748 | 662553.375 | 443539.75 | 0 | 1121.6216 | 440919.3125 | 0 | 0 | 0 | 0 | 39199.616 | 0 | 0 | 39199.616 | 12013.5203 | 7011.6909 | -7272.7886 | 1.1757 | 0 | 101 | 2 | 12013.5203 | 1548134.0591 | 12013.5203
Htl-w04-v14-VRF_HR_OAU1 | Htl | CZ04 | 14 | VRF_HR_OAU1 | 688.3589 | 3673781.75 | 566447.625 | 0 | 1692748 | 591951.5625 | 380593.25 | 0 | 1121.6216 | 440918.4375 | 0 | 0 | 0 | 0 | 39199.616 | 0 | 0 | 39199.616 | 10977.1786 | 7011.6519 | -7272.7466 | 1.1757 | 0 | 101 | 2 | 10977.1786 | 1414584.8716 | 10977.1786
Htl-w04-v14-VRF_HR_OAU2 | Htl | CZ04 | 14 | VRF_HR_OAU2 | 645.2029 | 3568011 | 566447.625 | 0 | 1692748 | 533306.1875 | 333469.5625 | 0 | 1121.6216 | 440917.375 | 0 | 0 | 0 | 0 | 39199.616 | 0 | 0 | 39199.616 | 10156.4024 | 7011.6118 | -7272.7056 | 1.1757 | 0 | 101 | 2 | 10156.4024 | 1308814.7466 | 10156.4024
OfS-w05-v14-AC_S1Std | OfS | CZ05 | 14 | AC_S1Std | 30.1289 | 93462.5547 | 31593.9805 | 0 | 50648.0078 | 0 | 4150.4956 | 0 | 0 | 7070.145 | 0 | 0 | 0 | 0 | 358.0543 | 0 | 169.4187 | 188.6355 | 104.014 | 187.9314 | -286.056 | 0 | 0 | 0 | 0 | 104.014 | 11220.6406 | 87.0722
OfS-w05-v14-AC_S0Std | OfS | CZ05 | 14 | AC_S0Std | 30.2608 | 97156.7266 | 31593.9805 | 0 | 50648.0078 | 0 | 7845.2251 | 0 | 0 | 7069.605 | 0 | 0 | 0 | 0 | 357.8159 | 0 | 169.1816 | 188.6342 | 132.6572 | 187.9489 | -286.0393 | 0 | 0 | 0 | 0 | 132.6572 | 14914.8301 | 115.7391
OfS-w05-v14-AC_SHi | OfS | CZ05 | 14 | AC_SHi | 27.7745 | 89291.0703 | 31593.9805 | 0 | 50648.0078 | 0 | 3223.5742 | 0 | 0 | 3825.5884 | 0 | 0 | 0 | 0 | 381.6728 | 0 | 192.9902 | 188.6826 | 74.0005 | 186.4575 | -281.6245 | 0 | 0 | 0 | 0 | 74.0005 | 7049.1626 | 54.7015
OfS-w05-v14-AC_EStd | OfS | CZ05 | 14 | AC_EStd | 30.7889 | 92517.1797 | 31593.9805 | 0 | 50648.0078 | 0 | 4416.1919 | 0 | 0 | 5859.0796 | 0 | 0 | 0 | 0 | 370.8838 | 0 | 182.2138 | 188.67 | 97.9575 | 187.5216 | -278.5914 | 0 | 0 | 0 | 0 | 97.9575 | 10275.2715 | 79.7361
OfS-w05-v14-AC_EHi | OfS | CZ05 | 14 | AC_EHi | 29.3213 | 91749.2578 | 31593.9805 | 0 | 50648.0078 | 0 | 3648.2629 | 0 | 0 | 5859.0796 | 0 | 0 | 0 | 0 | 370.8838 | 0 | 182.2138 | 188.67 | 91.9984 | 187.5216 | -278.5914 | 0 | 0 | 0 | 0 | 91.9984 | 9507.3425 | 73.777
OfS-w05-v14-PVAV_Std | OfS | CZ05 | 14 | PVAV_Std | 32.9901 | 95055.3281 | 31593.9805 | 0 | 50648.0078 | 19.267 | 8240.793 | 0 | 250.8606 | 4302.4141 | 0 | 0 | 0 | 0 | 460.7363 | 0 | 272.2216 | 188.5148 | 126.6536 | 0 | 0 | 0 | 0 | 0 | 0 | 126.6536 | 12813.3346 | 99.4315
OfS-w05-v14-PVAV_Hi | OfS | CZ05 | 14 | PVAV_Hi | 30.5436 | 93145.0703 | 31593.9805 | 0 | 50648.0078 | 34.488 | 6265.457 | 0 | 251.2665 | 4351.9004 | 0 | 0 | 0 | 0 | 370.4115 | 0 | 181.8926 | 188.5189 | 102.7974 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7974 | 10903.1119 | 84.6081
OfS-w05-v14-VRF_HP_OAU0 | OfS | CZ05 | 14 | VRF_HP_OAU0 | 29.3567 | 95856.4766 | 31593.9805 | 0 | 50648.0078 | 1558.5337 | 7748.8306 | 0 | 0 | 4307.2056 | 0 | 0 | 0 | 0 | 188.6437 | 0 | 0 | 188.6437 | 105.6491 | 210.0628 | -219.5686 | 0 | 0 | 0 | 0 | 105.6491 | 13614.5698 | 105.6491
OfS-w05-v14-VRF_HP_OAU1 | OfS | CZ05 | 14 | VRF_HP_OAU1 | 28.4383 | 94812.7031 | 31593.9805 | 0 | 50648.0078 | 1414.9033 | 6848.6997 | 0 | 0 | 4307.2056 | 0 | 0 | 0 | 0 | 188.6437 | 0 | 0 | 188.6437 | 97.5495 | 210.0628 | -219.5686 | 0 | 0 | 0 | 0 | 97.5495 | 12570.8086 | 97.5495
OfS-w05-v14-VRF_HP_OAU2 | OfS | CZ05 | 14 | VRF_HP_OAU2 | 27.7014 | 93926.5312 | 31593.9805 | 0 | 50648.0078 | 1287.3616 | 6090.0781 | 0 | 0 | 4307.2056 | 0 | 0 | 0 | 0 | 188.6437 | 0 | 0 | 188.6437 | 90.6728 | 210.0628 | -219.5686 | 0 | 0 | 0 | 0 | 90.6728 | 11684.6453 | 90.6728
OfS-w05-v14-VRF_HR_OAU0 | OfS | CZ05 | 14 | VRF_HR_OAU0 | 28.8604 | 94961.6406 | 31593.9805 | 0 | 50648.0078 | 1269.3711 | 7136.2456 | 0 | 0 | 4314.1245 | 0 | 0 | 0 | 0 | 188.6342 | 0 | 0 | 188.6342 | 98.7052 | 211.0312 | -220.5697 | 0 | 0 | 0 | 0 | 98.7052 | 12719.7412 | 98.7052
OfS-w05-v14-VRF_HR_OAU1 | OfS | CZ05 | 14 | VRF_HR_OAU1 | 27.7478 | 94042.0703 | 31593.9805 | 0 | 50648.0078 | 1149.0042 | 6337.041 | 0 | 0 | 4314.1245 | 0 | 0 | 0 | 0 | 188.6342 | 0 | 0 | 188.6342 | 91.5693 | 211.0312 | -220.5697 | 0 | 0 | 0 | 0 | 91.5693 | 11800.1697 | 91.5693
OfS-w05-v14-VRF_HR_OAU2 | OfS | CZ05 | 14 | VRF_HR_OAU2 | 27.0882 | 93237.6172 | 31593.9805 | 0 | 50648.0078 | 1042.3671 | 5639.2275 | 0 | 0 | 4314.1245 | 0 | 0 | 0 | 0 | 188.6342 | 0 | 0 | 188.6342 | 85.3268 | 211.0312 | -220.5697 | 0 | 0 | 0 | 0 | 85.3268 | 10995.7191 | 85.3268
OfL-w05-v14-FPFC_1 | OfL | CZ05 | 14 | FPFC_1 | 453.487 | 1698153.75 | 500422.4062 | 0 | 883691.5 | 254.3531 | 183004.4375 | 3315.4749 | 57654.6016 | 69812.4219 | 0 | 0 | 0 | 0 | 6463.44 | 0 | 3300.3635 | 3163.0771 | 2741.2687 | 2918.4592 | -6042.6533 | 0 | 0 | 0 | 0 | 2741.2687 | 310725.814 | 2411.2323
OfL-w05-v14-FPFC_2 | OfL | CZ05 | 14 | FPFC_2 | 431.7918 | 1651819 | 500422.4062 | 0 | 883691.5 | 508.8506 | 133897.875 | 6061.0718 | 57595.8047 | 69643.3438 | 0 | 0 | 0 | 0 | 4994.9891 | 0 | 1831.8806 | 3163.1078 | 2213.56 | 2918.4592 | -6042.6533 | 0 | 0 | 0 | 0 | 2213.56 | 261645.8741 | 2030.372
OfL-w05-v14-VRF_HP_OAU0 | OfL | CZ05 | 14 | VRF_HP_OAU0 | 483.8961 | 1652499.75 | 500422.4062 | 0 | 883691.5 | 7915.5127 | 183438.5938 | 0 | 213.4769 | 76819.8281 | 0 | 0 | 0 | 0 | 3162.9085 | 0 | 0 | 3162.9085 | 2082.6863 | 3732.1743 | -3901.1418 | 0 | 0 | 0 | 0 | 2082.6863 | 268387.4114 | 2082.6863
OfL-w05-v14-VRF_HP_OAU1 | OfL | CZ05 | 14 | VRF_HP_OAU1 | 457.5725 | 1618959 | 500422.4062 | 0 | 883691.5 | 6809.4165 | 151004.4844 | 0 | 213.4769 | 76819.8281 | 0 | 0 | 0 | 0 | 3162.9085 | 0 | 0 | 3162.9085 | 1822.4143 | 3732.1743 | -3901.1418 | 0 | 0 | 0 | 0 | 1822.4143 | 234847.2059 | 1822.4143
OfL-w05-v14-VRF_HP_OAU2 | OfL | CZ05 | 14 | VRF_HP_OAU2 | 442.9832 | 1600438 | 500422.4062 | 0 | 883691.5 | 6154.5576 | 133138 | 0 | 213.4769 | 76819.8281 | 0 | 0 | 0 | 0 | 3162.9085 | 0 | 0 | 3162.9085 | 1678.6887 | 3732.1743 | -3901.1418 | 0 | 0 | 0 | 0 | 1678.6887 | 216325.8626 | 1678.6887
OfL-w05-v14-VRF_HR_OAU0 | OfL | CZ05 | 14 | VRF_HR_OAU0 | 481.0333 | 1640997.75 | 500422.4062 | 0 | 883691.5 | 6450.667 | 174012.8438 | 0 | 213.4769 | 76208.0938 | 0 | 0 | 0 | 0 | 3162.8736 | 0 | 0 | 3162.8736 | 1993.4282 | 3664.6289 | -3830.1799 | 0 | 0 | 0 | 0 | 1993.4282 | 256885.0814 | 1993.4282
OfL-w05-v14-VRF_HR_OAU1 | OfL | CZ05 | 14 | VRF_HR_OAU1 | 455.0973 | 1609156.125 | 500422.4062 | 0 | 883691.5 | 5530.916 | 143091.5625 | 0 | 213.4769 | 76208.0938 | 0 | 0 | 0 | 0 | 3162.8736 | 0 | 0 | 3162.8736 | 1746.3418 | 3664.6289 | -3830.1799 | 0 | 0 | 0 | 0 | 1746.3418 | 225044.0491 | 1746.3418
OfL-w05-v14-VRF_HR_OAU2 | OfL | CZ05 | 14 | VRF_HR_OAU2 | 440.8018 | 1591693.375 | 500422.4062 | 0 | 883691.5 | 4995.0918 | 126164.75 | 0 | 213.4769 | 76208.0938 | 0 | 0 | 0 | 0 | 3162.8736 | 0 | 0 | 3162.8736 | 1610.8318 | 3664.6289 | -3830.1799 | 0 | 0 | 0 | 0 | 1610.8318 | 207581.4124 | 1610.8318
EPr-w05-v14-AC_S1Std | EPr | CZ05 | 14 | AC_S1Std | 123.8822 | 293798.8438 | 133157.6562 | 0 | 99493.7734 | 0 | 16459.6523 | 0 | 0 | 44688.3359 | 0 | 0 | 0 | 0 | 10419.2755 | 110.3944 | 7986.6573 | 2322.2254 | 1273.1741 | 1100.3119 | -2469.9045 | 0 | 0 | 0 | 0 | 1273.1741 | 61147.9883 | 474.5084
EPr-w05-v14-AC_S0Std | EPr | CZ05 | 14 | AC_S0Std | 123.9866 | 295413.375 | 133157.6562 | 0 | 99493.7734 | 0 | 18074.207 | 0 | 0 | 44688.3359 | 0 | 0 | 0 | 0 | 10419.1744 | 110.3944 | 7986.5568 | 2322.2251 | 1285.693 | 1100.3121 | -2469.9045 | 0 | 0 | 0 | 0 | 1285.693 | 62762.543 | 487.0373
EPr-w05-v14-AC_SHi | EPr | CZ05 | 14 | AC_SHi | 112.9536 | 279789.3125 | 133157.6562 | 0 | 99493.7734 | 0 | 13055.7217 | 0 | 0 | 34082.7344 | 0 | 0 | 0 | 0 | 10642.665 | 110.3944 | 8209.9104 | 2322.3594 | 1186.7855 | 1087.5238 | -2465.4634 | 0 | 0 | 0 | 0 | 1186.7855 | 47138.4561 | 365.7944
EPr-w05-v14-AC_EStd | EPr | CZ05 | 14 | AC_EStd | 127.581 | 294716.0625 | 133157.6562 | 0 | 99493.7734 | 0 | 17851.9609 | 0 | 0 | 44213.3203 | 0 | 0 | 0 | 0 | 10396.4006 | 110.3944 | 7963.6691 | 2322.3376 | 1277.9935 | 1106.5448 | -2452.8911 | 0 | 0 | 0 | 0 | 1277.9935 | 62065.2812 | 481.6266
EPr-w05-v14-AC_EHi | EPr | CZ05 | 14 | AC_EHi | 120.8216 | 291611.7812 | 133157.6562 | 0 | 99493.7734 | 0 | 14747.6953 | 0 | 0 | 44213.3203 | 0 | 0 | 0 | 0 | 10396.4006 | 110.3944 | 7963.6691 | 2322.3376 | 1253.9044 | 1106.5448 | -2452.8911 | 0 | 0 | 0 | 0 | 1253.9044 | 58961.0156 | 457.5375
EPr-w05-v14-PVAV_Std | EPr | CZ05 | 14 | PVAV_Std | 131.86 | 303127.3125 | 133157.6562 | 0 | 99493.7734 | 214.2997 | 27164.2949 | 0 | 444.7548 | 42652.7031 | 0 | 0 | 0 | 0 | 10772.5325 | 110.3944 | 8339.2 | 2322.94 | 1380.8142 | 1136.6606 | -961.3936 | 0 | 0 | 0 | 0 | 1380.8142 | 70476.0525 | 546.8942
EPr-w05-v14-PVAV_Hi | EPr | CZ05 | 14 | PVAV_Hi | 121.6198 | 296602.0938 | 133157.6562 | 0 | 99493.7734 | 407.8612 | 21075.6816 | 0 | 460.7067 | 42006.6875 | 0 | 0 | 0 | 0 | 10251.4733 | 110.3944 | 7818.0685 | 2323.0125 | 1278.0661 | 1121.5425 | -957.176 | 0 | 0 | 0 | 0 | 1278.0661 | 63950.9371 | 496.2593
EPr-w05-v14-VRF_HP_OAU0 | EPr | CZ05 | 14 | VRF_HP_OAU0 | 128.2902 | 343380.3438 | 133157.6562 | 0 | 99493.7734 | 44326.043 | 17618.5332 | 0 | 0 | 48784.4805 | 0 | 0 | 0 | 0 | 2432.3555 | 110.3944 | 0 | 2321.9611 | 859.2575 | 1089.5944 | -1138.1432 | 0.15285 | 0 | 0 | 4 | 859.2575 | 110729.0566 | 859.2575
EPr-w05-v14-VRF_HP_OAU1 | EPr | CZ05 | 14 | VRF_HP_OAU1 | 123.7844 | 337134.375 | 133157.6562 | 0 | 99493.7734 | 40140.2734 | 15558.5508 | 0 | 0 | 48784.4805 | 0 | 0 | 0 | 0 | 2432.3555 | 110.3944 | 0 | 2321.9611 | 810.7904 | 1089.5944 | -1138.1432 | 0.15285 | 0 | 0 | 4 | 810.7904 | 104483.3047 | 810.7904
EPr-w05-v14-VRF_HP_OAU2 | EPr | CZ05 | 14 | VRF_HP_OAU2 | 119.9089 | 331704.5938 | 133157.6562 | 0 | 99493.7734 | 36452.3516 | 13816.8018 | 0 | 0 | 48784.4805 | 0 | 0 | 0 | 0 | 2432.3555 | 110.3944 | 0 | 2321.9611 | 768.6562 | 1089.5944 | -1138.1432 | 0.15285 | 0 | 0 | 4 | 768.6562 | 99053.6338 | 768.6562
EPr-w05-v14-VRF_HR_OAU0 | EPr | CZ05 | 14 | VRF_HR_OAU0 | 124.3877 | 335575.75 | 133157.6562 | 0 | 99493.7734 | 38049.4414 | 16148.2412 | 0 | 0 | 48727.0156 | 0 | 0 | 0 | 0 | 2432.3536 | 110.3944 | 0 | 2321.9594 | 798.6957 | 1076.9205 | -1124.2559 | 0.53496 | 0 | 0 | 14 | 798.6957 | 102924.6982 | 798.6957
EPr-w05-v14-VRF_HR_OAU1 | EPr | CZ05 | 14 | VRF_HR_OAU1 | 119.4398 | 329972.75 | 133157.6562 | 0 | 99493.7734 | 34339.0547 | 14255.8096 | 0 | 0 | 48727.0156 | 0 | 0 | 0 | 0 | 2432.3536 | 110.3944 | 0 | 2321.9594 | 755.2178 | 1076.9205 | -1124.2559 | 0.53496 | 0 | 0 | 14 | 755.2178 | 97321.8799 | 755.2178
EPr-w05-v14-VRF_HR_OAU2 | EPr | CZ05 | 14 | VRF_HR_OAU2 | 116.4475 | 325121.8438 | 133157.6562 | 0 | 99493.7734 | 31062.6113 | 12681.3906 | 0 | 0 | 48727.0156 | 0 | 0 | 0 | 0 | 2432.3536 | 110.3944 | 0 | 2321.9594 | 717.5751 | 1076.9205 | -1124.2559 | 0.53496 | 0 | 0 | 14 | 717.5751 | 92471.0176 | 717.5751
Htl-w05-v14-FPFC_1 | Htl | CZ05 | 14 | FPFC_1 | 522.9859 | 3286392 | 566447.625 | 0 | 1692748 | 10222.6016 | 382569.8438 | 5972.8364 | 193529.625 | 434900.5938 | 0 | 0 | 0 | 0 | 177394.9542 | 0 | 135639.511 | 41755.3971 | 21488.639 | 6267.9414 | -11486.1396 | 0 | 0 | 0 | 0 | 21488.639 | 1021222.6641 | 7924.6879
Htl-w05-v14-FPFC_2 | Htl | CZ05 | 14 | FPFC_2 | 488.3011 | 3190901.5 | 566447.625 | 0 | 1692748 | 21966.957 | 268476.0625 | 11840.127 | 193597.0625 | 435824.75 | 0 | 0 | 0 | 0 | 154712.1459 | 0 | 112956.7437 | 41755.4253 | 18433.8255 | 6267.9414 | -11486.1396 | 0.60495 | 0 | 0 | 53 | 18433.8255 | 919864.832 | 7138.1511
Htl-w05-v14-VRF_HP_OAU0 | Htl | CZ05 | 14 | VRF_HP_OAU0 | 541.9229 | 3760854.75 | 566447.625 | 0 | 1692748 | 836765.4375 | 241563 | 0 | 1121.6216 | 422208.125 | 0 | 0 | 0 | 0 | 41755.5686 | 0 | 0 | 41755.5686 | 11652.8675 | 5963.3716 | -6196.0405 | 0.33101 | 0 | 29 | 0 | 11652.8675 | 1501658.1841 | 11652.8675
Htl-w05-v14-VRF_HP_OAU1 | Htl | CZ05 | 14 | VRF_HP_OAU1 | 511.8399 | 3636325.5 | 566447.625 | 0 | 1692748 | 748685 | 205113.8438 | 0 | 1121.6216 | 422208.2188 | 0 | 0 | 0 | 0 | 41755.5686 | 0 | 0 | 41755.5686 | 10686.5186 | 5963.3462 | -6196.0132 | 0.33101 | 0 | 29 | 0 | 10686.5186 | 1377128.6841 | 10686.5186
Htl-w05-v14-VRF_HP_OAU2 | Htl | CZ05 | 14 | VRF_HP_OAU2 | 489.9726 | 3536370.75 | 566447.625 | 0 | 1692748 | 675398 | 178447.3281 | 0 | 1121.6216 | 422208.2188 | 0 | 0 | 0 | 0 | 41755.5686 | 0 | 0 | 41755.5686 | 9910.8793 | 5963.3208 | -6195.9873 | 0.33101 | 0 | 29 | 0 | 9910.8793 | 1277175.1685 | 9910.8793
Htl-w05-v14-VRF_HR_OAU0 | Htl | CZ05 | 14 | VRF_HR_OAU0 | 525.9209 | 3648833.75 | 566447.625 | 0 | 1692748 | 740037.5625 | 226349.9844 | 0 | 1121.6216 | 422127.7812 | 0 | 0 | 0 | 0 | 41755.5917 | 0 | 0 | 41755.5917 | 10783.5827 | 5923.6353 | -6154.2251 | 1.267 | 0 | 90 | 21 | 10783.5827 | 1389636.9497 | 10783.5827
Htl-w05-v14-VRF_HR_OAU1 | Htl | CZ05 | 14 | VRF_HR_OAU1 | 498.0431 | 3534305.75 | 566447.625 | 0 | 1692748 | 659360.9375 | 192499.4219 | 0 | 1121.6216 | 422127.8438 | 0 | 0 | 0 | 0 | 41755.5917 | 0 | 0 | 41755.5917 | 9894.8522 | 5923.6016 | -6154.1909 | 1.267 | 0 | 90 | 21 | 9894.8522 | 1275109.8247 | 9894.8522
Htl-w05-v14-VRF_HR_OAU2 | Htl | CZ05 | 14 | VRF_HR_OAU2 | 477.8394 | 3443263 | 566447.625 | 0 | 1692748 | 592594.0625 | 168223.1875 | 0 | 1121.6216 | 422127.8438 | 0 | 0 | 0 | 0 | 41755.5917 | 0 | 0 | 41755.5917 | 9188.3577 | 5923.5684 | -6154.1558 | 1.267 | 0 | 90 | 21 | 9188.3577 | 1184066.7153 | 9188.3577
OfS-w06-v14-AC_S1Std | OfS | CZ06 | 14 | AC_S1Std | 35.258 | 101299.7031 | 31593.9805 | 0 | 50648.0078 | 0 | 10480.6201 | 0 | 0 | 8577.1943 | 0 | 0 | 0 | 0 | 220.1916 | 0 | 44.3835 | 175.8081 | 152.327 | 236.4085 | -335.4419 | 0 | 0 | 0 | 0 | 152.327 | 19057.8145 | 147.8886
OfS-w06-v14-AC_S0Std | OfS | CZ06 | 14 | AC_S0Std | 35.2581 | 105074.5703 | 31593.9805 | 0 | 50648.0078 | 0 | 14255.5244 | 0 | 0 | 8577.1533 | 0 | 0 | 0 | 0 | 220.1084 | 0 | 44.3012 | 175.8072 | 181.6117 | 236.4097 | -335.4411 | 0 | 0 | 0 | 0 | 181.6117 | 22832.6777 | 177.1816
OfS-w06-v14-AC_SHi | OfS | CZ06 | 14 | AC_SHi | 32.3828 | 95366.9922 | 31593.9805 | 0 | 50648.0078 | 0 | 8624.5986 | 0 | 0 | 4500.4897 | 0 | 0 | 0 | 0 | 229.6278 | 0 | 53.76 | 175.8677 | 107.2267 | 234.2216 | -314.5165 | 0 | 0 | 0 | 0 | 107.2267 | 13125.0884 | 101.8507
OfS-w06-v14-AC_EStd | OfS | CZ06 | 14 | AC_EStd | 37.0013 | 100973.6406 | 31593.9805 | 0 | 50648.0078 | 0 | 11601.4697 | 0 | 0 | 7130.2983 | 0 | 0 | 0 | 0 | 224.6994 | 0 | 48.8478 | 175.8516 | 150.2433 | 236.337 | -310.9433 | 0 | 0 | 0 | 0 | 150.2433 | 18731.7681 | 145.3585
OfS-w06-v14-AC_EHi | OfS | CZ06 | 14 | AC_EHi | 34.5889 | 98956.2656 | 31593.9805 | 0 | 50648.0078 | 0 | 9584.0977 | 0 | 0 | 7130.2983 | 0 | 0 | 0 | 0 | 224.6994 | 0 | 48.8478 | 175.8516 | 134.5885 | 236.337 | -310.9433 | 0 | 0 | 0 | 0 | 134.5885 | 16714.396 | 129.7037
OfS-w06-v14-PVAV_Std | OfS | CZ06 | 14 | PVAV_Std | 39.39 | 104350.2344 | 31593.9805 | 0 | 50648.0078 | 8.6544 | 17279.7637 | 0 | 110.2945 | 4709.6138 | 0 | 0 | 0 | 0 | 292.7454 | 0 | 116.8145 | 175.9309 | 183.2421 | 0 | 0 | 0 | 0 | 0 | 0 | 183.2421 | 22108.3263 | 171.5606
OfS-w06-v14-PVAV_Hi | OfS | CZ06 | 14 | PVAV_Hi | 35.4785 | 100214.3906 | 31593.9805 | 0 | 50648.0078 | 16.012 | 13105.7793 | 0 | 111.3798 | 4739.292 | 0 | 0 | 0 | 0 | 248.8425 | 0 | 72.9107 | 175.9318 | 146.7574 | 0 | 0 | 0 | 0 | 0 | 0 | 146.7574 | 17972.4631 | 139.4663
OfS-w06-v14-VRF_HP_OAU0 | OfS | CZ06 | 14 | VRF_HP_OAU0 | 34.9187 | 101261.9297 | 31593.9805 | 0 | 50648.0078 | 471.6616 | 13701.0918 | 0 | 0 | 4847.2876 | 0 | 0 | 0 | 0 | 175.8461 | 0 | 0 | 175.8461 | 147.5955 | 264.7291 | -276.3384 | 0 | 0 | 0 | 0 | 147.5955 | 19020.041 | 147.5955
OfS-w06-v14-VRF_HP_OAU1 | OfS | CZ06 | 14 | VRF_HP_OAU1 | 33.3196 | 99600.9219 | 31593.9805 | 0 | 50648.0078 | 426.7663 | 12084.9512 | 0 | 0 | 4847.2876 | 0 | 0 | 0 | 0 | 175.8461 | 0 | 0 | 175.8461 | 134.7059 | 264.7291 | -276.3384 | 0 | 0 | 0 | 0 | 134.7059 | 17359.0051 | 134.7059
OfS-w06-v14-VRF_HP_OAU2 | OfS | CZ06 | 14 | VRF_HP_OAU2 | 31.9898 | 98198.5547 | 31593.9805 | 0 | 50648.0078 | 386.9174 | 10722.4404 | 0 | 0 | 4847.2876 | 0 | 0 | 0 | 0 | 175.8461 | 0 | 0 | 175.8461 | 123.8236 | 264.7291 | -276.3384 | 0 | 0 | 0 | 0 | 123.8236 | 15956.6454 | 123.8236
OfS-w06-v14-VRF_HR_OAU0 | OfS | CZ06 | 14 | VRF_HR_OAU0 | 34.8647 | 99933.7812 | 31593.9805 | 0 | 50648.0078 | 388.8785 | 12457.7012 | 0 | 0 | 4845.2891 | 0 | 0 | 0 | 0 | 175.8206 | 0 | 0 | 175.8206 | 137.2889 | 264.255 | -275.8398 | 0 | 0 | 0 | 0 | 137.2889 | 17691.8688 | 137.2889
OfS-w06-v14-VRF_HR_OAU1 | OfS | CZ06 | 14 | VRF_HR_OAU1 | 33.3256 | 98409.8594 | 31593.9805 | 0 | 50648.0078 | 348.1335 | 10974.5137 | 0 | 0 | 4845.2891 | 0 | 0 | 0 | 0 | 175.8206 | 0 | 0 | 175.8206 | 125.4632 | 264.255 | -275.8398 | 0 | 0 | 0 | 0 | 125.4632 | 16167.9362 | 125.4632
OfS-w06-v14-VRF_HR_OAU2 | OfS | CZ06 | 14 | VRF_HR_OAU2 | 32.0302 | 97126.1016 | 31593.9805 | 0 | 50648.0078 | 312.8351 | 9726.0801 | 0 | 0 | 4845.2891 | 0 | 0 | 0 | 0 | 175.8206 | 0 | 0 | 175.8206 | 115.5014 | 264.255 | -275.8398 | 0 | 0 | 0 | 0 | 115.5014 | 14884.2042 | 115.5014
OfL-w06-v14-FPFC_1 | OfL | CZ06 | 14 | FPFC_1 | 504.3471 | 1788755.875 | 500422.4062 | 0 | 883691.5 | 167.6149 | 253150.2188 | 5363.2446 | 72406.9062 | 73555.1719 | 0 | 0 | 0 | 0 | 5066.8547 | 0 | 2137.1117 | 2929.7424 | 3312.1233 | 4000.1829 | -7580.9727 | 0 | 0 | 0 | 0 | 3312.1233 | 399279.9118 | 3098.4121
OfL-w06-v14-FPFC_2 | OfL | CZ06 | 14 | FPFC_2 | 478.2634 | 1729221.875 | 500422.4062 | 0 | 883691.5 | 333.1674 | 187784.7969 | 11154.9326 | 72285.6953 | 73550.8594 | 0 | 0 | 0 | 0 | 3976.185 | 0 | 1046.4273 | 2929.7571 | 2696.1298 | 4000.1829 | -7580.9727 | 0 | 0 | 0 | 0 | 2696.1298 | 333954.519 | 2591.4871
OfL-w06-v14-VRF_HP_OAU0 | OfL | CZ06 | 14 | VRF_HP_OAU0 | 571.913 | 1748237 | 500422.4062 | 0 | 883691.5 | 2823.3745 | 275769.8438 | 0 | 213.4769 | 85317.0703 | 0 | 0 | 0 | 0 | 2929.2214 | 0 | 0 | 2929.2214 | 2825.6004 | 4447.752 | -4643.1929 | 0 | 0 | 0 | 0 | 2825.6004 | 364123.7654 | 2825.6004
OfL-w06-v14-VRF_HP_OAU1 | OfL | CZ06 | 14 | VRF_HP_OAU1 | 529.96 | 1698959.125 | 500422.4062 | 0 | 883691.5 | 2411.5938 | 226904.4219 | 0 | 213.4769 | 85317.0703 | 0 | 0 | 0 | 0 | 2929.2214 | 0 | 0 | 2929.2214 | 2443.2093 | 4447.752 | -4643.1929 | 0 | 0 | 0 | 0 | 2443.2093 | 314846.5628 | 2443.2093
OfL-w06-v14-VRF_HP_OAU2 | OfL | CZ06 | 14 | VRF_HP_OAU2 | 506.932 | 1671821 | 500422.4062 | 0 | 883691.5 | 2170.0764 | 200007.7656 | 0 | 213.4769 | 85317.0703 | 0 | 0 | 0 | 0 | 2929.2214 | 0 | 0 | 2929.2214 | 2232.6171 | 4447.752 | -4643.1929 | 0 | 0 | 0 | 0 | 2232.6171 | 287708.3892 | 2232.6171
OfL-w06-v14-VRF_HR_OAU0 | OfL | CZ06 | 14 | VRF_HR_OAU0 | 571.5601 | 1725647.625 | 500422.4062 | 0 | 883691.5 | 2288.8066 | 253206.7031 | 0 | 213.4769 | 85825.8359 | 0 | 0 | 0 | 0 | 2929.1866 | 0 | 0 | 2929.1866 | 2650.3102 | 4528.939 | -4727.5923 | 0 | 0 | 0 | 0 | 2650.3102 | 341534.8226 | 2650.3102
OfL-w06-v14-VRF_HR_OAU1 | OfL | CZ06 | 14 | VRF_HR_OAU1 | 530.3149 | 1680286.5 | 500422.4062 | 0 | 883691.5 | 1938.5649 | 208196.2656 | 0 | 213.4769 | 85825.8438 | 0 | 0 | 0 | 0 | 2929.1866 | 0 | 0 | 2929.1866 | 2298.3114 | 4528.939 | -4727.5923 | 0 | 0 | 0 | 0 | 2298.3114 | 296174.1512 | 2298.3114
OfL-w06-v14-VRF_HR_OAU2 | OfL | CZ06 | 14 | VRF_HR_OAU2 | 507.517 | 1655348.875 | 500422.4062 | 0 | 883691.5 | 1736.5164 | 183460.9375 | 0 | 213.4769 | 85825.7891 | 0 | 0 | 0 | 0 | 2929.1866 | 0 | 0 | 2929.1866 | 2104.7969 | 4528.939 | -4727.5923 | 0 | 0 | 0 | 0 | 2104.7969 | 271236.7198 | 2104.7969
EPr-w06-v14-AC_S1Std | EPr | CZ06 | 14 | AC_S1Std | 161.1534 | 317832.8125 | 133157.6562 | 0 | 99493.7734 | 0 | 34625.8828 | 0 | 0 | 50555.8906 | 0 | 0 | 0 | 0 | 6417.7715 | 110.3944 | 4153.7789 | 2153.5982 | 1076.3884 | 1403.1027 | -2634.7874 | 0.26748 | 0 | 7 | 0 | 1076.3884 | 85181.7734 | 661.0106
EPr-w06-v14-AC_S0Std | EPr | CZ06 | 14 | AC_S0Std | 161.1535 | 322701.375 | 133157.6562 | 0 | 99493.7734 | 0 | 39494.2617 | 0 | 0 | 50555.9688 | 0 | 0 | 0 | 0 | 6417.6083 | 110.3944 | 4153.6163 | 2153.5976 | 1114.1514 | 1403.1072 | -2634.7947 | 0.26748 | 0 | 7 | 0 | 1114.1514 | 90050.2305 | 698.7898
EPr-w06-v14-AC_SHi | EPr | CZ06 | 14 | AC_SHi | 146.1448 | 299095.3438 | 133157.6562 | 0 | 99493.7734 | 0 | 28588.6875 | 0 | 0 | 37855.8594 | 0 | 0 | 0 | 0 | 6550.2778 | 110.3944 | 4286.1533 | 2153.7307 | 944.225 | 1403.5753 | -2522.8054 | 0.076423 | 0 | 2 | 0 | 944.225 | 66444.5469 | 515.6097
EPr-w06-v14-AC_EStd | EPr | CZ06 | 14 | AC_EStd | 174.1384 | 322651.0625 | 133157.6562 | 0 | 99493.7734 | 0 | 38943.6328 | 0 | 0 | 51056.1758 | 0 | 0 | 0 | 0 | 6362.759 | 110.3944 | 4098.6614 | 2153.704 | 1108.2647 | 1437.9952 | -2541.9473 | 0.26748 | 0 | 7 | 0 | 1108.2647 | 89999.8086 | 698.3985
EPr-w06-v14-AC_EHi | EPr | CZ06 | 14 | AC_EHi | 160.0915 | 315879.2188 | 133157.6562 | 0 | 99493.7734 | 0 | 32171.75 | 0 | 0 | 51056.1758 | 0 | 0 | 0 | 0 | 6362.759 | 110.3944 | 4098.6614 | 2153.704 | 1055.7148 | 1437.9952 | -2541.9473 | 0.26748 | 0 | 7 | 0 | 1055.7148 | 83227.9258 | 645.8487
EPr-w06-v14-PVAV_Std | EPr | CZ06 | 14 | PVAV_Std | 177.0567 | 326026.9375 | 133157.6562 | 0 | 99493.7734 | 113.0237 | 49747.3945 | 0 | 228.8805 | 43286.2773 | 0 | 0 | 0 | 0 | 6800.7936 | 110.3944 | 4535.9648 | 2154.4328 | 1178.191 | 1509.2129 | -997.7038 | 0.076423 | 0 | 2 | 0 | 1178.191 | 93375.5761 | 724.5945
EPr-w06-v14-PVAV_Hi | EPr | CZ06 | 14 | PVAV_Hi | 156.3724 | 314027.6875 | 133157.6562 | 0 | 99493.7734 | 226.1109 | 38740.2266 | 0 | 235.0803 | 42174.8828 | 0 | 0 | 0 | 0 | 6603.9936 | 110.3944 | 4339.1235 | 2154.4749 | 1065.3924 | 1497.7124 | -983.3453 | 0 | 0 | 0 | 0 | 1065.3924 | 81376.3005 | 631.4801
EPr-w06-v14-VRF_HP_OAU0 | EPr | CZ06 | 14 | VRF_HP_OAU0 | 165.5972 | 341700.0312 | 133157.6562 | 0 | 99493.7734 | 21003.832 | 36918.0039 | 0 | 0 | 51126.8242 | 0 | 0 | 0 | 0 | 2263.7285 | 110.3944 | 0 | 2153.3339 | 846.2176 | 1415.2002 | -1476.0255 | 0.038212 | 0 | 1 | 0 | 846.2176 | 109048.6602 | 846.2176
EPr-w06-v14-VRF_HP_OAU1 | EPr | CZ06 | 14 | VRF_HP_OAU1 | 156.5564 | 335362.75 | 133157.6562 | 0 | 99493.7734 | 18996.8516 | 32588.2578 | 0 | 0 | 51126.3047 | 0 | 0 | 0 | 0 | 2263.7285 | 110.3944 | 0 | 2153.3341 | 797.0406 | 1415.2002 | -1476.0255 | 0.038212 | 0 | 1 | 0 | 797.0406 | 102711.4141 | 797.0406
EPr-w06-v14-VRF_HP_OAU2 | EPr | CZ06 | 14 | VRF_HP_OAU2 | 149.0937 | 329928.0312 | 133157.6562 | 0 | 99493.7734 | 17221.0039 | 28929.7852 | 0 | 0 | 51126.0625 | 0 | 0 | 0 | 0 | 2263.7285 | 110.3944 | 0 | 2153.3341 | 754.8684 | 1415.2002 | -1476.0255 | 0.038212 | 0 | 1 | 0 | 754.8684 | 97276.8516 | 754.8684
EPr-w06-v14-VRF_HR_OAU0 | EPr | CZ06 | 14 | VRF_HR_OAU0 | 158.9985 | 335063.0312 | 133157.6562 | 0 | 99493.7734 | 17803.0977 | 33516.0859 | 0 | 0 | 51092.5469 | 0 | 0 | 0 | 0 | 2263.716 | 110.3944 | 0 | 2153.3218 | 794.715 | 1406.7474 | -1467.144 | 0.038212 | 0 | 1 | 0 | 794.715 | 102411.7305 | 794.715
EPr-w06-v14-VRF_HR_OAU1 | EPr | CZ06 | 14 | VRF_HR_OAU1 | 150.7964 | 329384.3125 | 133157.6562 | 0 | 99493.7734 | 16035.8369 | 29604.8027 | 0 | 0 | 51092.5469 | 0 | 0 | 0 | 0 | 2263.716 | 110.3944 | 0 | 2153.3218 | 750.6495 | 1406.7474 | -1467.144 | 0.038212 | 0 | 1 | 0 | 750.6495 | 96733.1865 | 750.6495
EPr-w06-v14-VRF_HR_OAU2 | EPr | CZ06 | 14 | VRF_HR_OAU2 | 144.0569 | 324558.4688 | 133157.6562 | 0 | 99493.7734 | 14493.3223 | 26321.6172 | 0 | 0 | 51092.5469 | 0 | 0 | 0 | 0 | 2263.716 | 110.3944 | 0 | 2153.3218 | 713.2021 | 1406.7474 | -1467.144 | 0.038212 | 0 | 1 | 0 | 713.2021 | 91907.4863 | 713.2021
Htl-w06-v14-FPFC_1 | Htl | CZ06 | 14 | FPFC_1 | 603.1594 | 3668484 | 566447.625 | 0 | 1692748 | 6902.124 | 589201.0625 | 10615.377 | 271184.75 | 531383.9375 | 0 | 0 | 0 | 0 | 125879.511 | 0 | 88235.7453 | 37643.7862 | 19677.2683 | 7893.7148 | -15334.0928 | 0 | 0 | 0 | 0 | 19677.2683 | 1398671.874 | 10853.6937
Htl-w06-v14-FPFC_2 | Htl | CZ06 | 14 | FPFC_2 | 563.4849 | 3525176.5 | 566447.625 | 0 | 1692748 | 19360.9629 | 417282.8438 | 26167.791 | 271491.5625 | 531676.9375 | 0 | 0 | 0 | 0 | 107531.5507 | 0 | 69887.8464 | 37643.7299 | 16609.7281 | 7893.7148 | -15334.0928 | 0 | 0 | 0 | 0 | 16609.7281 | 1239812.3066 | 9620.9435
Htl-w06-v14-VRF_HP_OAU0 | Htl | CZ06 | 14 | VRF_HP_OAU0 | 661.5298 | 3586188.5 | 566447.625 | 0 | 1692748 | 445297.9688 | 438956.875 | 0 | 1121.6216 | 441615.625 | 0 | 0 | 0 | 0 | 37643.8656 | 0 | 0 | 37643.8656 | 10297.4586 | 6766.2988 | -7018.2119 | 0.034243 | 0 | 3 | 0 | 10297.4586 | 1326992.0903 | 10297.4586
Htl-w06-v14-VRF_HP_OAU1 | Htl | CZ06 | 14 | VRF_HP_OAU1 | 614.8466 | 3473885.75 | 566447.625 | 0 | 1692748 | 398297.8438 | 373653.8125 | 0 | 1121.6216 | 441615.5938 | 0 | 0 | 0 | 0 | 37643.8656 | 0 | 0 | 37643.8656 | 9425.9856 | 6766.2949 | -7018.2075 | 0.034243 | 0 | 3 | 0 | 9425.9856 | 1214688.8716 | 9425.9856
Htl-w06-v14-VRF_HP_OAU2 | Htl | CZ06 | 14 | VRF_HP_OAU2 | 580.7201 | 3386339.25 | 566447.625 | 0 | 1692748 | 358899.8438 | 325505.4375 | 0 | 1121.6216 | 441615.5312 | 0 | 0 | 0 | 0 | 37643.8656 | 0 | 0 | 37643.8656 | 8746.6253 | 6766.2949 | -7018.207 | 0.034243 | 0 | 3 | 0 | 8746.6253 | 1127142.4341 | 8746.6253
Htl-w06-v14-VRF_HR_OAU0 | Htl | CZ06 | 14 | VRF_HR_OAU0 | 644.6546 | 3499994.5 | 566447.625 | 0 | 1692748 | 391771.375 | 406470.4062 | 0 | 1121.6216 | 441434.7812 | 0 | 0 | 0 | 0 | 37643.7914 | 0 | 0 | 37643.7914 | 9628.5939 | 6738.9722 | -6990.0981 | 0.82182 | 0 | 69 | 3 | 9628.5939 | 1240798.1841 | 9628.5939
Htl-w06-v14-VRF_HR_OAU1 | Htl | CZ06 | 14 | VRF_HR_OAU1 | 599.5163 | 3399312 | 566447.625 | 0 | 1692748 | 349650.6875 | 347908.4688 | 0 | 1121.6216 | 441434.4062 | 0 | 0 | 0 | 0 | 37643.7914 | 0 | 0 | 37643.7914 | 8847.2938 | 6738.9805 | -6990.1064 | 0.82182 | 0 | 69 | 3 | 8847.2938 | 1140115.1841 | 8847.2938
Htl-w06-v14-VRF_HR_OAU2 | Htl | CZ06 | 14 | VRF_HR_OAU2 | 566.535 | 3320872.5 | 566447.625 | 0 | 1692748 | 314603 | 304517.4688 | 0 | 1121.6216 | 441434.3438 | 0 | 0 | 0 | 0 | 37643.7914 | 0 | 0 | 37643.7914 | 8238.6091 | 6738.9731 | -6990.0991 | 0.82182 | 0 | 69 | 3 | 8238.6091 | 1061676.4341 | 8238.6091
OfS-w07-v14-AC_S1Std | OfS | CZ07 | 14 | AC_S1Std | 33.3826 | 99218.0078 | 31593.9805 | 0 | 50648.0078 | 0 | 8726.9883 | 0 | 0 | 8249.0957 | 0 | 0 | 0 | 0 | 184.7916 | 0 | 10.7258 | 174.0657 | 132.807 | 223.8192 | -302.6981 | 0 | 0 | 0 | 0 | 132.807 | 16976.084 | 131.7344
OfS-w07-v14-AC_S0Std | OfS | CZ07 | 14 | AC_S0Std | 33.3826 | 104310.1875 | 31593.9805 | 0 | 50648.0078 | 0 | 13819.2158 | 0 | 0 | 8249.0977 | 0 | 0 | 0 | 0 | 184.7488 | 0 | 10.6844 | 174.0644 | 172.3186 | 223.8178 | -302.6981 | 0 | 0 | 0 | 0 | 172.3186 | 22068.3135 | 171.2501
OfS-w07-v14-AC_SHi | OfS | CZ07 | 14 | AC_SHi | 30.8524 | 94028.9844 | 31593.9805 | 0 | 50648.0078 | 0 | 7220.667 | 0 | 0 | 4566.4116 | 0 | 0 | 0 | 0 | 188.3452 | 0 | 14.2238 | 174.1214 | 92.8901 | 221.3789 | -288.3198 | 0 | 0 | 0 | 0 | 92.8901 | 11787.0786 | 91.4677
OfS-w07-v14-AC_EStd | OfS | CZ07 | 14 | AC_EStd | 35.0125 | 99184.4219 | 31593.9805 | 0 | 50648.0078 | 0 | 9674.377 | 0 | 0 | 7268.1587 | 0 | 0 | 0 | 0 | 186.3685 | 0 | 12.2623 | 174.1062 | 132.7003 | 226.5504 | -284.8411 | 0 | 0 | 0 | 0 | 132.7003 | 16942.5356 | 131.4741
OfS-w07-v14-AC_EHi | OfS | CZ07 | 14 | AC_EHi | 32.9086 | 97502.1562 | 31593.9805 | 0 | 50648.0078 | 0 | 7992.1064 | 0 | 0 | 7268.1587 | 0 | 0 | 0 | 0 | 186.3685 | 0 | 12.2623 | 174.1062 | 119.6459 | 226.5504 | -284.8411 | 0 | 0 | 0 | 0 | 119.6459 | 15260.2651 | 118.4197
OfS-w07-v14-PVAV_Std | OfS | CZ07 | 14 | PVAV_Std | 37.2875 | 102835.6953 | 31593.9805 | 0 | 50648.0078 | 3.2972 | 15932.9189 | 0 | 29.1563 | 4628.4502 | 0 | 0 | 0 | 0 | 217.5297 | 0 | 43.2694 | 174.2602 | 164.135 | 0 | 0 | 0 | 0 | 0 | 0 | 164.135 | 20593.8226 | 159.8081
OfS-w07-v14-PVAV_Hi | OfS | CZ07 | 14 | PVAV_Hi | 33.7936 | 99048.5703 | 31593.9805 | 0 | 50648.0078 | 5.9258 | 12113.1543 | 0 | 28.9512 | 4658.6323 | 0 | 0 | 0 | 0 | 198.2576 | 0 | 23.9969 | 174.2607 | 132.8194 | 0 | 0 | 0 | 0 | 0 | 0 | 132.8194 | 16806.6636 | 130.4197
OfS-w07-v14-VRF_HP_OAU0 | OfS | CZ07 | 14 | VRF_HP_OAU0 | 32.9332 | 100426.6172 | 31593.9805 | 0 | 50648.0078 | 163.6478 | 13229.1504 | 0 | 0 | 4791.9121 | 0 | 0 | 0 | 0 | 174.1169 | 0 | 0 | 174.1169 | 141.1134 | 259.1264 | -270.7664 | 0 | 0 | 0 | 0 | 141.1134 | 18184.7103 | 141.1134
OfS-w07-v14-VRF_HP_OAU1 | OfS | CZ07 | 14 | VRF_HP_OAU1 | 31.6171 | 98834.1172 | 31593.9805 | 0 | 50648.0078 | 147.8461 | 11652.4414 | 0 | 0 | 4791.9121 | 0 | 0 | 0 | 0 | 174.1169 | 0 | 0 | 174.1169 | 128.7555 | 259.1264 | -270.7664 | 0 | 0 | 0 | 0 | 128.7555 | 16592.1996 | 128.7555
OfS-w07-v14-VRF_HP_OAU2 | OfS | CZ07 | 14 | VRF_HP_OAU2 | 30.5096 | 97499.5938 | 31593.9805 | 0 | 50648.0078 | 134.0778 | 10331.6973 | 0 | 0 | 4791.9121 | 0 | 0 | 0 | 0 | 174.1169 | 0 | 0 | 174.1169 | 118.3997 | 259.1264 | -270.7664 | 0 | 0 | 0 | 0 | 118.3997 | 15257.6871 | 118.3997
OfS-w07-v14-VRF_HR_OAU0 | OfS | CZ07 | 14 | VRF_HR_OAU0 | 32.6948 | 99354.125 | 31593.9805 | 0 | 50648.0078 | 127.6465 | 12197.3428 | 0 | 0 | 4787.229 | 0 | 0 | 0 | 0 | 174.093 | 0 | 0 | 174.093 | 132.7908 | 258.2537 | -269.8861 | 0 | 0 | 0 | 0 | 132.7908 | 17112.2183 | 132.7908
OfS-w07-v14-VRF_HR_OAU1 | OfS | CZ07 | 14 | VRF_HR_OAU1 | 31.41 | 97884.1484 | 31593.9805 | 0 | 50648.0078 | 114.0822 | 10740.9492 | 0 | 0 | 4787.229 | 0 | 0 | 0 | 0 | 174.093 | 0 | 0 | 174.093 | 121.3839 | 258.2537 | -269.8861 | 0 | 0 | 0 | 0 | 121.3839 | 15642.2604 | 121.3839
OfS-w07-v14-VRF_HR_OAU2 | OfS | CZ07 | 14 | VRF_HR_OAU2 | 30.3282 | 96649.2734 | 31593.9805 | 0 | 50648.0078 | 102.5556 | 9517.5938 | 0 | 0 | 4787.229 | 0 | 0 | 0 | 0 | 174.093 | 0 | 0 | 174.093 | 111.8013 | 258.2537 | -269.8861 | 0 | 0 | 0 | 0 | 111.8013 | 14407.3784 | 111.8013
OfL-w07-v14-FPFC_1 | OfL | CZ07 | 14 | FPFC_1 | 499.7202 | 1791413.25 | 500422.4062 | 0 | 883691.5 | 86.3072 | 255164.7969 | 5219.1543 | 74338.125 | 72492.1562 | 0 | 0 | 0 | 0 | 3999.3597 | 0 | 1100.4283 | 2898.9322 | 3230.1944 | 3659.6221 | -6597.6118 | 0 | 0 | 0 | 0 | 3230.1944 | 402081.3853 | 3120.1516
OfL-w07-v14-FPFC_2 | OfL | CZ07 | 14 | FPFC_2 | 474.728 | 1730617.25 | 500422.4062 | 0 | 883691.5 | 165.7091 | 188872.2031 | 10745.5615 | 74267.3672 | 72453.8281 | 0 | 0 | 0 | 0 | 3394.9158 | 0 | 495.9742 | 2898.9418 | 2655.0881 | 3659.6221 | -6597.6118 | 0 | 0 | 0 | 0 | 2655.0881 | 335759.1076 | 2605.4907
OfL-w07-v14-VRF_HP_OAU0 | OfL | CZ07 | 14 | VRF_HP_OAU0 | 543.9774 | 1734554 | 500422.4062 | 0 | 883691.5 | 785.8928 | 264685.6562 | 0 | 213.4769 | 84756.4219 | 0 | 0 | 0 | 0 | 2898.4698 | 0 | 0 | 2898.4698 | 2719.4256 | 4432.8906 | -4635.6611 | 0 | 0 | 0 | 0 | 2719.4256 | 350441.4478 | 2719.4256
OfL-w07-v14-VRF_HP_OAU1 | OfL | CZ07 | 14 | VRF_HP_OAU1 | 507.5477 | 1687503 | 500422.4062 | 0 | 883691.5 | 669.5625 | 217751.4062 | 0 | 213.4769 | 84756.4219 | 0 | 0 | 0 | 0 | 2898.4698 | 0 | 0 | 2898.4698 | 2354.3131 | 4432.8906 | -4635.6611 | 0 | 0 | 0 | 0 | 2354.3131 | 303390.8675 | 2354.3131
OfL-w07-v14-VRF_HP_OAU2 | OfL | CZ07 | 14 | VRF_HP_OAU2 | 487.4075 | 1661581.625 | 500422.4062 | 0 | 883691.5 | 601.0217 | 191898.6719 | 0 | 213.4769 | 84756.4219 | 0 | 0 | 0 | 0 | 2898.4698 | 0 | 0 | 2898.4698 | 2153.164 | 4432.8906 | -4635.6611 | 0 | 0 | 0 | 0 | 2153.164 | 277469.5923 | 2153.164
OfL-w07-v14-VRF_HR_OAU0 | OfL | CZ07 | 14 | VRF_HR_OAU0 | 547.4134 | 1717497 | 500422.4062 | 0 | 883691.5 | 573.9694 | 248592.7969 | 0 | 213.4769 | 84003.7812 | 0 | 0 | 0 | 0 | 2898.432 | 0 | 0 | 2898.432 | 2587.06 | 4310.8257 | -4507.96 | 0 | 0 | 0 | 0 | 2587.06 | 333384.0244 | 2587.06
OfL-w07-v14-VRF_HR_OAU1 | OfL | CZ07 | 14 | VRF_HR_OAU1 | 510.4171 | 1673210.5 | 500422.4062 | 0 | 883691.5 | 484.351 | 204396.375 | 0 | 213.4769 | 84003.7812 | 0 | 0 | 0 | 0 | 2898.432 | 0 | 0 | 2898.432 | 2243.4004 | 4310.8257 | -4507.96 | 0 | 0 | 0 | 0 | 2243.4004 | 289097.9841 | 2243.4004
OfL-w07-v14-VRF_HR_OAU2 | OfL | CZ07 | 14 | VRF_HR_OAU2 | 489.9534 | 1648873.375 | 500422.4062 | 0 | 883691.5 | 433.2198 | 180110.6562 | 0 | 213.4769 | 84003.7812 | 0 | 0 | 0 | 0 | 2898.432 | 0 | 0 | 2898.432 | 2054.5464 | 4310.8257 | -4507.96 | 0 | 0 | 0 | 0 | 2054.5464 | 264761.1341 | 2054.5464
EPr-w07-v14-AC_S1Std | EPr | CZ07 | 14 | AC_S1Std | 148.1381 | 310765.7188 | 133157.6562 | 0 | 99493.7734 | 0 | 25365.4355 | 0 | 0 | 52749.5039 | 0 | 0 | 0 | 0 | 5587.2685 | 110.3944 | 3348.015 | 2128.8573 | 940.9734 | 1465.4015 | -2529.2144 | 0 | 0 | 0 | 0 | 940.9734 | 78114.9395 | 606.1719
EPr-w07-v14-AC_S0Std | EPr | CZ07 | 14 | AC_S0Std | 148.1381 | 318887.0625 | 133157.6562 | 0 | 99493.7734 | 0 | 33486.5664 | 0 | 0 | 52749.5039 | 0 | 0 | 0 | 0 | 5586.9862 | 110.3944 | 3347.7354 | 2128.8566 | 1003.9654 | 1465.4015 | -2529.2144 | 0 | 0 | 0 | 0 | 1003.9654 | 86236.0703 | 669.1919
EPr-w07-v14-AC_SHi | EPr | CZ07 | 14 | AC_SHi | 133.7056 | 292307.1875 | 133157.6562 | 0 | 99493.7734 | 0 | 21095.4258 | 0 | 0 | 38560.8633 | 0 | 0 | 0 | 0 | 5702.5312 | 110.3944 | 3463.1341 | 2129.0022 | 809.2462 | 1436.6779 | -2248.3523 | 0 | 0 | 0 | 0 | 809.2462 | 59656.2891 | 462.9328
EPr-w07-v14-AC_EStd | EPr | CZ07 | 14 | AC_EStd | 157.6978 | 313670.5625 | 133157.6562 | 0 | 99493.7734 | 0 | 28429.8945 | 0 | 0 | 52589.9922 | 0 | 0 | 0 | 0 | 5501.2851 | 110.3944 | 3261.9158 | 2128.975 | 954.9059 | 1528.3602 | -2249.9067 | 0 | 0 | 0 | 0 | 954.9059 | 81019.8867 | 628.7143
EPr-w07-v14-AC_EHi | EPr | CZ07 | 14 | AC_EHi | 146.3116 | 308726.9375 | 133157.6562 | 0 | 99493.7734 | 0 | 23486.2363 | 0 | 0 | 52589.9922 | 0 | 0 | 0 | 0 | 5501.2851 | 110.3944 | 3261.9158 | 2128.975 | 916.5431 | 1528.3602 | -2249.9067 | 0 | 0 | 0 | 0 | 916.5431 | 76076.2285 | 590.3515
EPr-w07-v14-PVAV_Std | EPr | CZ07 | 14 | PVAV_Std | 160.2012 | 315993.7188 | 133157.6562 | 0 | 99493.7734 | 70.2683 | 39770.7461 | 0 | 85.2326 | 43416.6484 | 0 | 0 | 0 | 0 | 5882.0403 | 110.3944 | 3641.8874 | 2129.759 | 1010.9296 | 1554.1995 | -882.5275 | 0 | 0 | 0 | 0 | 1010.9296 | 83342.8955 | 646.7409
EPr-w07-v14-PVAV_Hi | EPr | CZ07 | 14 | PVAV_Hi | 143.5844 | 306388.8125 | 133157.6562 | 0 | 99493.7734 | 130.4783 | 31284.5195 | 0 | 87.2004 | 42235.8359 | 0 | 0 | 0 | 0 | 5889.1712 | 110.3944 | 3648.9994 | 2129.7768 | 937.1071 | 1523.272 | -875.7237 | 0 | 0 | 0 | 0 | 937.1071 | 73738.0342 | 572.2071
EPr-w07-v14-VRF_HP_OAU0 | EPr | CZ07 | 14 | VRF_HP_OAU0 | 145.8362 | 331790.1875 | 133157.6562 | 0 | 99493.7734 | 16631.9199 | 29636.8457 | 0 | 0 | 52870.668 | 0 | 0 | 0 | 0 | 2239.019 | 110.3944 | 0 | 2128.6245 | 769.322 | 1634.2548 | -1708.65 | 0 | 0 | 0 | 0 | 769.322 | 99139.4336 | 769.322
EPr-w07-v14-VRF_HP_OAU1 | EPr | CZ07 | 14 | VRF_HP_OAU1 | 139.5118 | 326678.2812 | 133157.6562 | 0 | 99493.7734 | 15039.0986 | 26117.9199 | 0 | 0 | 52870.668 | 0 | 0 | 0 | 0 | 2239.019 | 110.3944 | 0 | 2128.6245 | 729.6548 | 1634.2548 | -1708.65 | 0 | 0 | 0 | 0 | 729.6548 | 94027.6865 | 729.6548
EPr-w07-v14-VRF_HP_OAU2 | EPr | CZ07 | 14 | VRF_HP_OAU2 | 134.186 | 322322.1562 | 133157.6562 | 0 | 99493.7734 | 13641.9141 | 23158.9434 | 0 | 0 | 52870.668 | 0 | 0 | 0 | 0 | 2239.019 | 110.3944 | 0 | 2128.6245 | 695.851 | 1634.2548 | -1708.65 | 0 | 0 | 0 | 0 | 695.851 | 89671.5254 | 695.851
EPr-w07-v14-VRF_HR_OAU0 | EPr | CZ07 | 14 | VRF_HR_OAU0 | 139.5154 | 326292.4375 | 133157.6562 | 0 | 99493.7734 | 13992.9404 | 26834.0469 | 0 | 0 | 52814.75 | 0 | 0 | 0 | 0 | 2239.007 | 110.3944 | 0 | 2128.6123 | 726.6599 | 1623.6324 | -1697.4565 | 0.038212 | 0 | 1 | 0 | 726.6599 | 93641.7373 | 726.6599
EPr-w07-v14-VRF_HR_OAU1 | EPr | CZ07 | 14 | VRF_HR_OAU1 | 133.9307 | 321695.1562 | 133157.6562 | 0 | 99493.7734 | 12589.748 | 23640 | 0 | 0 | 52814.75 | 0 | 0 | 0 | 0 | 2239.007 | 110.3944 | 0 | 2128.6123 | 690.9853 | 1623.6324 | -1697.4565 | 0.038212 | 0 | 1 | 0 | 690.9853 | 89044.498 | 690.9853
EPr-w07-v14-VRF_HR_OAU2 | EPr | CZ07 | 14 | VRF_HR_OAU2 | 129.2277 | 317787.3438 | 133157.6562 | 0 | 99493.7734 | 11361.8086 | 20960.1387 | 0 | 0 | 52814.75 | 0 | 0 | 0 | 0 | 2239.007 | 110.3944 | 0 | 2128.6123 | 660.6608 | 1623.6324 | -1697.4565 | 0.038212 | 0 | 1 | 0 | 660.6608 | 85136.6973 | 660.6608
Htl-w07-v14-FPFC_1 | Htl | CZ07 | 14 | FPFC_1 | 565.3547 | 3619428.5 | 566447.625 | 0 | 1692748 | 5224.0337 | 595740.75 | 10477.2861 | 281759.1562 | 467031.1875 | 0 | 0 | 0 | 0 | 103839.4675 | 0 | 66736.0205 | 37103.4342 | 17147.7018 | 6971.165 | -11523.1826 | 0 | 0 | 0 | 0 | 17147.7018 | 1349755.1274 | 10474.0998
Htl-w07-v14-FPFC_2 | Htl | CZ07 | 14 | FPFC_2 | 531.3513 | 3469502.25 | 566447.625 | 0 | 1692748 | 14686.1689 | 420321.25 | 26372.3574 | 282034.6875 | 466891.5312 | 0 | 0 | 0 | 0 | 90434.3142 | 0 | 53330.9491 | 37103.3677 | 14520.4199 | 6971.165 | -11523.1826 | 0 | 0 | 0 | 0 | 14520.4199 | 1183933.6377 | 9187.325
Htl-w07-v14-VRF_HP_OAU0 | Htl | CZ07 | 14 | VRF_HP_OAU0 | 586.3513 | 3404922.5 | 566447.625 | 0 | 1692748 | 299823.1562 | 406391.8125 | 0 | 1121.6216 | 438389.75 | 0 | 0 | 0 | 0 | 37103.2371 | 0 | 0 | 37103.2371 | 8890.8364 | 6472.5601 | -6718.1362 | 0.1598 | 0 | 14 | 0 | 8890.8364 | 1145726.3403 | 8890.8364
Htl-w07-v14-VRF_HP_OAU1 | Htl | CZ07 | 14 | VRF_HP_OAU1 | 550.5527 | 3311787.5 | 566447.625 | 0 | 1692748 | 268561.2812 | 344518.1875 | 0 | 1121.6216 | 438389.75 | 0 | 0 | 0 | 0 | 37103.2371 | 0 | 0 | 37103.2371 | 8168.1049 | 6472.5601 | -6718.1362 | 0.1598 | 0 | 14 | 0 | 8168.1049 | 1052590.8403 | 8168.1049
Htl-w07-v14-VRF_HP_OAU2 | Htl | CZ07 | 14 | VRF_HP_OAU2 | 523.8713 | 3240294.25 | 566447.625 | 0 | 1692748 | 242271.2812 | 299314.7812 | 0 | 1121.6216 | 438389.75 | 0 | 0 | 0 | 0 | 37103.2371 | 0 | 0 | 37103.2371 | 7613.3161 | 6472.5601 | -6718.1362 | 0.1598 | 0 | 14 | 0 | 7613.3161 | 981097.4341 | 7613.3161
Htl-w07-v14-VRF_HR_OAU0 | Htl | CZ07 | 14 | VRF_HR_OAU0 | 573.1324 | 3338953 | 566447.625 | 0 | 1692748 | 264923.9688 | 375752.5625 | 0 | 1121.6216 | 437958.125 | 0 | 0 | 0 | 0 | 37103.145 | 0 | 0 | 37103.145 | 8378.9087 | 6440.0986 | -6684.2852 | 0.61637 | 0 | 49 | 5 | 8378.9087 | 1079756.2778 | 8378.9087
Htl-w07-v14-VRF_HR_OAU1 | Htl | CZ07 | 14 | VRF_HR_OAU1 | 538.9573 | 3252381.5 | 566447.625 | 0 | 1692748 | 236013.5938 | 318092.0312 | 0 | 1121.6216 | 437958.125 | 0 | 0 | 0 | 0 | 37103.145 | 0 | 0 | 37103.145 | 7707.1185 | 6440.0986 | -6684.2852 | 0.61637 | 0 | 49 | 5 | 7707.1185 | 993185.3716 | 7707.1185
Htl-w07-v14-VRF_HR_OAU2 | Htl | CZ07 | 14 | VRF_HR_OAU2 | 513.835 | 3186567.5 | 566447.625 | 0 | 1692748 | 212172.5156 | 276118.8125 | 0 | 1121.6216 | 437958.125 | 0 | 0 | 0 | 0 | 37103.145 | 0 | 0 | 37103.145 | 7196.3995 | 6440.0986 | -6684.2852 | 0.61637 | 0 | 49 | 5 | 7196.3995 | 927371.0747 | 7196.3995
OfS-w08-v14-AC_S1Std | OfS | CZ08 | 14 | AC_S1Std | 38.3445 | 104673.5938 | 31593.9805 | 0 | 50648.0078 | 0 | 12958.3994 | 0 | 0 | 9473.2959 | 0 | 0 | 0 | 0 | 206.5941 | 0 | 35.0054 | 171.5887 | 177.5705 | 274.5963 | -360.925 | 0 | 0 | 0 | 0 | 177.5705 | 22431.6953 | 174.07
OfS-w08-v14-AC_S0Std | OfS | CZ08 | 14 | AC_S0Std | 38.3444 | 108797.2656 | 31593.9805 | 0 | 50648.0078 | 0 | 17082.1523 | 0 | 0 | 9473.2373 | 0 | 0 | 0 | 0 | 206.5457 | 0 | 34.9579 | 171.5878 | 209.5656 | 274.5941 | -360.923 | 0 | 0 | 0 | 0 | 209.5656 | 26555.3896 | 206.0698
OfS-w08-v14-AC_SHi | OfS | CZ08 | 14 | AC_SHi | 34.5067 | 97604.1172 | 31593.9805 | 0 | 50648.0078 | 0 | 10443.4375 | 0 | 0 | 4918.7944 | 0 | 0 | 0 | 0 | 214.8065 | 0 | 43.1555 | 171.651 | 123.5265 | 273.3986 | -317.838 | 0 | 0 | 0 | 0 | 123.5265 | 15362.2319 | 119.2109
OfS-w08-v14-AC_EStd | OfS | CZ08 | 14 | AC_EStd | 39.8953 | 104113.8516 | 31593.9805 | 0 | 50648.0078 | 0 | 14096.4248 | 0 | 0 | 7775.5654 | 0 | 0 | 0 | 0 | 210.3096 | 0 | 38.6743 | 171.6354 | 173.5941 | 273.2961 | -314.0448 | 0 | 0 | 0 | 0 | 173.5941 | 21871.9902 | 169.7266
OfS-w08-v14-AC_EHi | OfS | CZ08 | 14 | AC_EHi | 37.0055 | 101662.6406 | 31593.9805 | 0 | 50648.0078 | 0 | 11645.2051 | 0 | 0 | 7775.5654 | 0 | 0 | 0 | 0 | 210.3096 | 0 | 38.6743 | 171.6354 | 154.5726 | 273.2961 | -314.0448 | 0 | 0 | 0 | 0 | 154.5726 | 19420.7705 | 150.7052
OfS-w08-v14-PVAV_Std | OfS | CZ08 | 14 | PVAV_Std | 42.4755 | 107462.2266 | 31593.9805 | 0 | 50648.0078 | 6.4335 | 20500.5977 | 0 | 79.9094 | 4633.3945 | 0 | 0 | 0 | 0 | 260.946 | 0 | 89.168 | 171.7779 | 204.6266 | 0 | 0 | 0 | 0 | 0 | 0 | 204.6266 | 25220.3351 | 195.7098
OfS-w08-v14-PVAV_Hi | OfS | CZ08 | 14 | PVAV_Hi | 37.6817 | 102546.1953 | 31593.9805 | 0 | 50648.0078 | 11.1776 | 15575.0615 | 0 | 80.1898 | 4637.8701 | 0 | 0 | 0 | 0 | 229.2553 | 0 | 57.4769 | 171.7784 | 163.309 | 0 | 0 | 0 | 0 | 0 | 0 | 163.309 | 20304.299 | 157.5614
OfS-w08-v14-VRF_HP_OAU0 | OfS | CZ08 | 14 | VRF_HP_OAU0 | 37.5952 | 104053.8906 | 31593.9805 | 0 | 50648.0078 | 413.6516 | 16387.4277 | 0 | 0 | 5010.9429 | 0 | 0 | 0 | 0 | 171.6173 | 0 | 0 | 171.6173 | 169.2613 | 282.2449 | -294.4751 | 0 | 0 | 0 | 0 | 169.2613 | 21812.0222 | 169.2613
OfS-w08-v14-VRF_HP_OAU1 | OfS | CZ08 | 14 | VRF_HP_OAU1 | 35.7216 | 102060.4922 | 31593.9805 | 0 | 50648.0078 | 372.661 | 14435.0283 | 0 | 0 | 5010.9429 | 0 | 0 | 0 | 0 | 171.6173 | 0 | 0 | 171.6173 | 153.7926 | 282.2449 | -294.4751 | 0 | 0 | 0 | 0 | 153.7926 | 19818.6322 | 153.7926
OfS-w08-v14-VRF_HP_OAU2 | OfS | CZ08 | 14 | VRF_HP_OAU2 | 34.1484 | 100389.4844 | 31593.9805 | 0 | 50648.0078 | 336.4799 | 12800.1719 | 0 | 0 | 5010.9429 | 0 | 0 | 0 | 0 | 171.6173 | 0 | 0 | 171.6173 | 140.8253 | 282.2449 | -294.4751 | 0 | 0 | 0 | 0 | 140.8253 | 18147.5947 | 140.8253
OfS-w08-v14-VRF_HR_OAU0 | OfS | CZ08 | 14 | VRF_HR_OAU0 | 37.0789 | 102654.3828 | 31593.9805 | 0 | 50648.0078 | 340.8357 | 15066.4004 | 0 | 0 | 5005.2627 | 0 | 0 | 0 | 0 | 171.5926 | 0 | 0 | 171.5926 | 158.401 | 280.6155 | -292.7953 | 0 | 0 | 0 | 0 | 158.401 | 20412.4988 | 158.401
OfS-w08-v14-VRF_HR_OAU1 | OfS | CZ08 | 14 | VRF_HR_OAU1 | 35.2705 | 100827.8672 | 31593.9805 | 0 | 50648.0078 | 305.3661 | 13275.3496 | 0 | 0 | 5005.2627 | 0 | 0 | 0 | 0 | 171.5926 | 0 | 0 | 171.5926 | 144.2272 | 280.6155 | -292.7953 | 0 | 0 | 0 | 0 | 144.2272 | 18585.9784 | 144.2272
OfS-w08-v14-VRF_HR_OAU2 | OfS | CZ08 | 14 | VRF_HR_OAU2 | 33.7517 | 99288.4844 | 31593.9805 | 0 | 50648.0078 | 275.6943 | 11765.6367 | 0 | 0 | 5005.2627 | 0 | 0 | 0 | 0 | 171.5926 | 0 | 0 | 171.5926 | 132.2816 | 280.6155 | -292.7953 | 0 | 0 | 0 | 0 | 132.2816 | 17046.5937 | 132.2816
OfL-w08-v14-FPFC_1 | OfL | CZ08 | 14 | FPFC_1 | 510.8841 | 1828623.5 | 500422.4062 | 0 | 883691.5 | 111.7093 | 280958.9688 | 5816.772 | 83533.6719 | 74089.125 | 0 | 0 | 0 | 0 | 4276.5181 | 0 | 1424.3074 | 2852.2112 | 3546.6921 | 3869.312 | -7087.4917 | 0 | 0 | 0 | 0 | 3546.6921 | 438693.4749 | 3404.2614
OfL-w08-v14-FPFC_2 | OfL | CZ08 | 14 | FPFC_2 | 483.7025 | 1762827.875 | 500422.4062 | 0 | 883691.5 | 217.8697 | 208136.75 | 12839.8701 | 83479.2812 | 74041.0078 | 0 | 0 | 0 | 0 | 3532.0557 | 0 | 679.8306 | 2852.225 | 2907.1723 | 3869.312 | -7087.4917 | 0 | 0 | 0 | 0 | 2907.1723 | 365874.9088 | 2839.1893
OfL-w08-v14-VRF_HP_OAU0 | OfL | CZ08 | 14 | VRF_HP_OAU0 | 603.8354 | 1785899.375 | 500422.4062 | 0 | 883691.5 | 1754.5933 | 313954.375 | 0 | 213.4769 | 85863.9375 | 0 | 0 | 0 | 0 | 2851.6618 | 0 | 0 | 2851.6618 | 3117.8623 | 4524.6167 | -4717.79 | 0 | 0 | 0 | 0 | 3117.8623 | 401786.3826 | 3117.8623
OfL-w08-v14-VRF_HP_OAU1 | OfL | CZ08 | 14 | VRF_HP_OAU1 | 556.37 | 1729977 | 500422.4062 | 0 | 883691.5 | 1496.6882 | 258290.2656 | 0 | 213.4769 | 85863.9375 | 0 | 0 | 0 | 0 | 2851.6618 | 0 | 0 | 2851.6618 | 2683.9075 | 4524.6167 | -4717.79 | 0 | 0 | 0 | 0 | 2683.9075 | 345864.3682 | 2683.9075
OfL-w08-v14-VRF_HP_OAU2 | OfL | CZ08 | 14 | VRF_HP_OAU2 | 530.2334 | 1699156 | 500422.4062 | 0 | 883691.5 | 1345.2794 | 227620.9375 | 0 | 213.4769 | 85863.9375 | 0 | 0 | 0 | 0 | 2851.6618 | 0 | 0 | 2851.6618 | 2444.7386 | 4524.6167 | -4717.79 | 0 | 0 | 0 | 0 | 2444.7386 | 315043.6313 | 2444.7386
OfL-w08-v14-VRF_HR_OAU0 | OfL | CZ08 | 14 | VRF_HR_OAU0 | 599.7673 | 1763648 | 500422.4062 | 0 | 883691.5 | 1410.5823 | 288344.3438 | 0 | 213.4769 | 89567.0859 | 0 | 0 | 0 | 0 | 2851.6464 | 0 | 0 | 2851.6464 | 2945.1954 | 4865.7949 | -5074.1201 | 0 | 0 | 0 | 0 | 2945.1954 | 379535.4888 | 2945.1954
OfL-w08-v14-VRF_HR_OAU1 | OfL | CZ08 | 14 | VRF_HR_OAU1 | 553.1279 | 1712165 | 500422.4062 | 0 | 883691.5 | 1190.9417 | 237081.0312 | 0 | 213.4769 | 89567.0859 | 0 | 0 | 0 | 0 | 2851.6464 | 0 | 0 | 2851.6464 | 2545.6877 | 4865.7949 | -5074.1201 | 0 | 0 | 0 | 0 | 2545.6877 | 328052.5357 | 2545.6877
OfL-w08-v14-VRF_HR_OAU2 | OfL | CZ08 | 14 | VRF_HR_OAU2 | 527.4609 | 1683870.875 | 500422.4062 | 0 | 883691.5 | 1066.9854 | 208911.2656 | 0 | 213.4769 | 89567.0859 | 0 | 0 | 0 | 0 | 2851.6464 | 0 | 0 | 2851.6464 | 2326.1284 | 4865.7949 | -5074.1201 | 0 | 0 | 0 | 0 | 2326.1284 | 299758.8138 | 2326.1284
EPr-w08-v14-AC_S1Std | EPr | CZ08 | 14 | AC_S1Std | 190.0201 | 341764.625 | 133157.6562 | 0 | 99493.7734 | 0 | 44160.8086 | 0 | 0 | 64952.5195 | 0 | 0 | 0 | 0 | 5834.6701 | 110.3944 | 3626.592 | 2097.6843 | 1209.3786 | 1964.5454 | -3443.9529 | 0.038212 | 0 | 1 | 0 | 1209.3786 | 109113.3281 | 846.7194
EPr-w08-v14-AC_S0Std | EPr | CZ08 | 14 | AC_S0Std | 190.0202 | 351793.125 | 133157.6562 | 0 | 99493.7734 | 0 | 54189.3867 | 0 | 0 | 64952.5117 | 0 | 0 | 0 | 0 | 5834.4525 | 110.3944 | 3626.3747 | 2097.6834 | 1287.1786 | 1964.5454 | -3443.9529 | 0.038212 | 0 | 1 | 0 | 1287.1786 | 119141.8984 | 924.5411
EPr-w08-v14-AC_SHi | EPr | CZ08 | 14 | AC_SHi | 164.5706 | 314183.9062 | 133157.6562 | 0 | 99493.7734 | 0 | 35181.9219 | 0 | 0 | 46350.9102 | 0 | 0 | 0 | 0 | 5929.7088 | 110.3944 | 3721.4838 | 2097.832 | 1004.8432 | 1947.0497 | -2839.949 | 0 | 0 | 0 | 0 | 1004.8432 | 81532.832 | 632.6948
EPr-w08-v14-AC_EStd | EPr | CZ08 | 14 | AC_EStd | 200.6805 | 345683.2812 | 133157.6562 | 0 | 99493.7734 | 0 | 48849.7109 | 0 | 0 | 64182.457 | 0 | 0 | 0 | 0 | 5704.8358 | 110.3944 | 3496.633 | 2097.8091 | 1226.7929 | 2004.9792 | -2883.6729 | 0.038212 | 0 | 1 | 0 | 1226.7929 | 113032.168 | 877.1296
EPr-w08-v14-AC_EHi | EPr | CZ08 | 14 | AC_EHi | 182.6414 | 337188.875 | 133157.6562 | 0 | 99493.7734 | 0 | 40355.2617 | 0 | 0 | 64182.457 | 0 | 0 | 0 | 0 | 5704.8358 | 110.3944 | 3496.633 | 2097.8091 | 1160.876 | 2004.9792 | -2883.6729 | 0.038212 | 0 | 1 | 0 | 1160.876 | 104537.7188 | 811.2127
EPr-w08-v14-PVAV_Std | EPr | CZ08 | 14 | PVAV_Std | 199.2999 | 344921.75 | 133157.6562 | 0 | 99493.7734 | 90.3175 | 61559.2891 | 0 | 157.4104 | 50463.3984 | 0 | 0 | 0 | 0 | 6086.7194 | 110.3944 | 3877.632 | 2098.6925 | 1258.9816 | 206051% | -132014% | 3.821% | 0% | 100% | 0% | 1258.9816 | 112270.4154 | 871.2184
EPr-w08-v14-PVAV_Hi | EPr | CZ08 | 14 | PVAV_Hi | 173.9864 | 329728.9062 | 133157.6562 | 0 | 99493.7734 | 166.6361 | 47917.1211 | 0 | 161.7271 | 48832.1016 | 0 | 0 | 0 | 0 | 5975.9232 | 110.3944 | 3766.8125 | 2098.7178 | 1130.0033 | 205243% | -129071% | 0% | 0% | 0% | 0% | 1130.0033 | 97077.5858 | 753.3221
EPr-w08-v14-VRF_HP_OAU0 | EPr | CZ08 | 14 | VRF_HP_OAU0 | 186.5554 | 356049.6562 | 133157.6562 | 0 | 99493.7734 | 18712.0898 | 49145.9258 | 0 | 0 | 55540.1719 | 0 | 0 | 0 | 0 | 2207.8205 | 110.3944 | 0 | 2097.4261 | 957.5699 | 187280% | -195065% | 0% | 0% | 0% | 0% | 957.5699 | 123398.1875 | 957.5699
EPr-w08-v14-VRF_HP_OAU1 | EPr | CZ08 | 14 | VRF_HP_OAU1 | 175.4443 | 348401.75 | 133157.6562 | 0 | 99493.7734 | 16909.3027 | 43300.9492 | 0 | 0 | 55540.1719 | 0 | 0 | 0 | 0 | 2207.8205 | 110.3944 | 0 | 2097.4261 | 898.2233 | 187280% | -195065% | 0% | 0% | 0% | 0% | 898.2233 | 115750.4238 | 898.2233
EPr-w08-v14-VRF_HP_OAU2 | EPr | CZ08 | 14 | VRF_HP_OAU2 | 165.981 | 341910.1562 | 133157.6562 | 0 | 99493.7734 | 15327.9668 | 38390.7148 | 0 | 0 | 55540.1719 | 0 | 0 | 0 | 0 | 2207.8205 | 110.3944 | 0 | 2097.4261 | 847.8487 | 187280% | -195065% | 0% | 0% | 0% | 0% | 847.8487 | 109258.8535 | 847.8487
EPr-w08-v14-VRF_HR_OAU0 | EPr | CZ08 | 14 | VRF_HR_OAU0 | 173.916 | 347836.0625 | 133157.6562 | 0 | 99493.7734 | 15898.9434 | 43939.3633 | 0 | 0 | 55346.3867 | 0 | 0 | 0 | 0 | 2207.8077 | 110.3944 | 0 | 2097.4136 | 893.8332 | 185665% | -193420% | 0% | 0% | 0% | 0% | 893.8332 | 115184.6934 | 893.8332
EPr-w08-v14-VRF_HR_OAU1 | EPr | CZ08 | 14 | VRF_HR_OAU1 | 164.281 | 340989.75 | 133157.6562 | 0 | 99493.7734 | 14287.8467 | 38704.1836 | 0 | 0 | 55346.3867 | 0 | 0 | 0 | 0 | 2207.8077 | 110.3944 | 0 | 2097.4136 | 840.7061 | 185665% | -193420% | 0% | 0% | 0% | 0% | 840.7061 | 108338.417 | 840.7061
EPr-w08-v14-VRF_HR_OAU2 | EPr | CZ08 | 14 | VRF_HR_OAU2 | 156.1852 | 335180.0625 | 133157.6562 | 0 | 99493.7734 | 12872.8555 | 34309.5117 | 0 | 0 | 55346.3867 | 0 | 0 | 0 | 0 | 2207.8077 | 110.3944 | 0 | 2097.4136 | 795.6231 | 185665% | -193420% | 0% | 0% | 0% | 0% | 795.6231 | 102528.7539 | 795.6231
Htl-w08-v14-FPFC_1 | Htl | CZ08 | 14 | FPFC_1 | 655.545 | 3858038 | 566447.625 | 0 | 1692748 | 6083.7236 | 694708.75 | 12250.5127 | 317824.9062 | 567973.1875 | 0 | 0 | 0 | 0 | 113914.7878 | 0 | 77633.4541 | 36281.3645 | 20075.2882 | 880480% | -1586682% | 0% | 0% | 0% | 0% | 20075.2882 | 1586590.5674 | 12311.9428
Htl-w08-v14-FPFC_2 | Htl | CZ08 | 14 | FPFC_2 | 609.803 | 3689526.75 | 566447.625 | 0 | 1692748 | 17368.0508 | 494661.9375 | 32045.582 | 318161.7812 | 568092.4375 | 0 | 0 | 0 | 0 | 97255.4342 | 0 | 60974.1619 | 36281.2877 | 16948.1016 | 880480% | -1586682% | 0% | 0% | 0% | 0% | 16948.1016 | 1398284.207 | 10850.6854
Htl-w08-v14-VRF_HP_OAU0 | Htl | CZ08 | 14 | VRF_HP_OAU0 | 781.0082 | 3653933.75 | 566447.625 | 0 | 1692748 | 379750.6562 | 563429.6875 | 0 | 1121.6216 | 450436.1562 | 0 | 0 | 0 | 0 | 36281.2416 | 0 | 0 | 36281.2416 | 10823.1678 | 765619% | -793672% | 17.12% | 0% | 1500% | 0% | 10823.1678 | 1394738.1216 | 10823.1678 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Htl-w08-v14-VRF_HP_OAU1 | Htl | CZ08 | 14 | VRF_HP_OAU1 | 717.6024 | 3529140.5 | 566447.625 | 0 | 1692748 | 339342.3125 | 479043.9062 | 0 | 1121.6216 | 450436.125 | 0 | 0 | 0 | 0 | 36281.2416 | 0 | 0 | 36281.2416 | 9854.7652 | 765619% | -793673% | 17.12% | 0% | 1500% | 0% | 9854.7652 | 1269943.9653 | 9854.7652 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Htl-w08-v14-VRF_HP_OAU2 | Htl | CZ08 | 14 | VRF_HP_OAU2 | 669.9186 | 3432986.5 | 566447.625 | 0 | 1692748 | 305344.4375 | 416888.0312 | 0 | 1121.6216 | 450436.1562 | 0 | 0 | 0 | 0 | 36281.2416 | 0 | 0 | 36281.2416 | 9108.6123 | 765619% | -793673% | 17.12% | 0% | 1500% | 0% | 9108.6123 | 1173790.2466 | 9108.6123
Htl-w08-v14-VRF_HR_OAU0 | Htl | CZ08 | 14 | VRF_HR_OAU0 | 760.9274 | 3575003.5 | 566447.625 | 0 | 1692748 | 336809.1875 | 528381.125 | 0 | 1121.6216 | 449495.3125 | 0 | 0 | 0 | 0 | 36281.1418 | 0 | 0 | 36281.1418 | 10210.6642 | 765511% | -793517% | 67.34% | 0% | 5800% | 100% | 10210.6642 | 1315807.2466 | 10210.6642
Htl-w08-v14-VRF_HR_OAU1 | Htl | CZ08 | 14 | VRF_HR_OAU1 | 698.9775 | 3458398.5 | 566447.625 | 0 | 1692748 | 299687.5 | 448897.6562 | 0 | 1121.6216 | 449495.3125 | 0 | 0 | 0 | 0 | 36281.1418 | 0 | 0 | 36281.1418 | 9305.8082 | 765511% | -793517% | 67.34% | 0% | 5800% | 100% | 9305.8082 | 1199202.0903 | 9305.8082
Htl-w08-v14-VRF_HR_OAU2 | Htl | CZ08 | 14 | VRF_HR_OAU2 | 653.9363 | 3369451 | 566447.625 | 0 | 1692748 | 269216.9375 | 390421.1562 | 0 | 1121.6216 | 449495.25 | 0 | 0 | 0 | 0 | 36281.1418 | 0 | 0 | 36281.1418 | 8615.5785 | 765511% | -793517% | 67.34% | 0% | 5800% | 100% | 8615.5785 | 1110254.9653 | 8615.5785
OfS-w09-v14-AC_S1Std | OfS | CZ09 | 14 | AC_S1Std | 43.918 | 107522.5312 | 31593.9805 | 0 | 50648.0078 | 0 | 14441.1904 | 0 | 0 | 10839.5234 | 0 | 0 | 0 | 0 | 208.0757 | 0 | 36.6984 | 171.3773 | 199.8482 | 32345% | -40281% | 0% | 0% | 0% | 0% | 199.8482 | 25280.7139 | 196.1783
OfS-w09-v14-AC_S0Std | OfS | CZ09 | 14 | AC_S0Std | 43.918 | 112137.4609 | 31593.9805 | 0 | 50648.0078 | 0 | 19056.1055 | 0 | 0 | 10839.5225 | 0 | 0 | 0 | 0 | 208.0082 | 0 | 36.6319 | 171.3764 | 235.6533 | 32345% | -40281% | 0% | 0% | 0% | 0% | 235.6533 | 29895.6279 | 231.9901
OfS-w09-v14-AC_SHi | OfS | CZ09 | 14 | AC_SHi | 38.8186 | 99124.3203 | 31593.9805 | 0 | 50648.0078 | 0 | 11365.6191 | 0 | 0 | 5516.8169 | 0 | 0 | 0 | 0 | 218.6052 | 0 | 47.1556 | 171.4497 | 135.7233 | 32498% | -33309% | 0% | 0% | 0% | 0% | 135.7233 | 16882.436 | 131.0077
OfS-w09-v14-AC_EStd | OfS | CZ09 | 14 | AC_EStd | 45.8512 | 106164.3438 | 31593.9805 | 0 | 50648.0078 | 0 | 15358.4082 | 0 | 0 | 8564.0459 | 0 | 0 | 0 | 0 | 212.0324 | 0 | 40.5995 | 171.4329 | 189.6982 | 32841% | -32905% | 0% | 0% | 0% | 0% | 189.6982 | 23922.4541 | 185.6382
OfS-w09-v14-AC_EHi | OfS | CZ09 | 14 | AC_EHi | 42.0052 | 103493.6797 | 31593.9805 | 0 | 50648.0078 | 0 | 12687.7471 | 0 | 0 | 8564.0459 | 0 | 0 | 0 | 0 | 212.0324 | 0 | 40.5995 | 171.4329 | 168.9739 | 32841% | -32905% | 0% | 0% | 0% | 0% | 168.9739 | 21251.793 | 164.9139
OfS-w09-v14-PVAV_Std | OfS | CZ09 | 14 | PVAV_Std | 48.7904 | 108377.4922 | 31593.9805 | 0 | 50648.0078 | 6.3909 | 20242.3066 | 0 | 113.8158 | 5773.0776 | 0 | 0 | 0 | 0 | 258.3064 | 0 | 86.8175 | 171.4889 | 211.4939 | 0% | 0% | 0% | 0% | 0% | 0% | 211.4939 | 26135.591 | 202.8122
OfS-w09-v14-PVAV_Hi | OfS | CZ09 | 14 | PVAV_Hi | 42.4158 | 103550.9609 | 31593.9805 | 0 | 50648.0078 | 11.7213 | 15351.0645 | 0 | 114.0379 | 5832.2354 | 0 | 0 | 0 | 0 | 227.1176 | 0 | 55.6324 | 171.4853 | 170.9215 | 0% | 0% | 0% | 0% | 0% | 0% | 170.9215 | 21309.059 | 165.3583
OfS-w09-v14-VRF_HP_OAU0 | OfS | CZ09 | 14 | VRF_HP_OAU0 | 43.5573 | 105939.9219 | 31593.9805 | 0 | 50648.0078 | 494.4865 | 17787.6289 | 0 | 0 | 5415.9463 | 0 | 0 | 0 | 0 | 171.4197 | 0 | 0 | 171.4197 | 183.897 | 32047% | -33416% | 0% | 0% | 0% | 0% | 183.897 | 23698.0616 | 183.897
OfS-w09-v14-VRF_HP_OAU1 | OfS | CZ09 | 14 | VRF_HP_OAU1 | 40.9736 | 103775.375 | 31593.9805 | 0 | 50648.0078 | 445.3463 | 15672.1992 | 0 | 0 | 5415.9463 | 0 | 0 | 0 | 0 | 171.4197 | 0 | 0 | 171.4197 | 167.0999 | 32047% | -33416% | 0% | 0% | 0% | 0% | 167.0999 | 21533.4918 | 167.0999
OfS-w09-v14-VRF_HP_OAU2 | OfS | CZ09 | 14 | VRF_HP_OAU2 | 38.8057 | 101951.7578 | 31593.9805 | 0 | 50648.0078 | 402.2104 | 13891.7324 | 0 | 0 | 5415.9463 | 0 | 0 | 0 | 0 | 171.4197 | 0 | 0 | 171.4197 | 152.9487 | 32047% | -33416% | 0% | 0% | 0% | 0% | 152.9487 | 19709.8891 | 152.9487
OfS-w09-v14-VRF_HR_OAU0 | OfS | CZ09 | 14 | VRF_HR_OAU0 | 42.86 | 104451 | 31593.9805 | 0 | 50648.0078 | 406.8786 | 16345.1982 | 0 | 0 | 5457.0303 | 0 | 0 | 0 | 0 | 171.3998 | 0 | 0 | 171.3998 | 172.3427 | 32374% | -33763% | 0% | 0% | 0% | 0% | 172.3427 | 22209.1071 | 172.3427
OfS-w09-v14-VRF_HR_OAU1 | OfS | CZ09 | 14 | VRF_HR_OAU1 | 40.3656 | 102460.6719 | 31593.9805 | 0 | 50648.0078 | 364.7633 | 14397.0127 | 0 | 0 | 5457.0303 | 0 | 0 | 0 | 0 | 171.3998 | 0 | 0 | 171.3998 | 156.8979 | 32374% | -33763% | 0% | 0% | 0% | 0% | 156.8979 | 20218.8063 | 156.8979
OfS-w09-v14-VRF_HR_OAU2 | OfS | CZ09 | 14 | VRF_HR_OAU2 | 38.2728 | 100786.3203 | 31593.9805 | 0 | 50648.0078 | 328.7008 | 12758.708 | 0 | 0 | 5457.0303 | 0 | 0 | 0 | 0 | 171.3998 | 0 | 0 | 171.3998 | 143.9048 | 32374% | -33763% | 0% | 0% | 0% | 0% | 143.9048 | 18544.4391 | 143.9048
OfL-w09-v14-FPFC_1 | OfL | CZ09 | 14 | FPFC_1 | 562.4598 | 1891440.625 | 500422.4062 | 0 | 883691.5 | 158.8718 | 321338.375 | 5466.2002 | 102252.6641 | 78110.8906 | 0 | 0 | 0 | 0 | 4874.6406 | 0 | 2025.6363 | 2849.0035 | 4097.0035 | 462272% | -801037% | 0% | 0% | 0% | 0% | 4097.0035 | 501860.8015 | 3894.4398
OfL-w09-v14-FPFC_2 | OfL | CZ09 | 14 | FPFC_2 | 530.6568 | 1809484.375 | 500422.4062 | 0 | 883691.5 | 316.7924 | 230022.25 | 14718.0342 | 102205.2734 | 78109.2188 | 0 | 0 | 0 | 0 | 3822.1885 | 0 | 973.1693 | 2849.0198 | 3283.9884 | 462272% | -801037% | 0% | 0% | 0% | 0% | 3283.9884 | 410653.5345 | 3186.6714
OfL-w09-v14-VRF_HP_OAU0 | OfL | CZ09 | 14 | VRF_HP_OAU0 | 723.0115 | 1812363.25 | 500422.4062 | 0 | 883691.5 | 2656.3977 | 331034.5938 | 0 | 213.4769 | 94346.1641 | 0 | 0 | 0 | 0 | 2848.4579 | 0 | 0 | 2848.4579 | 3323.2249 | 529160% | -551606% | 0% | 0% | 0% | 0% | 3323.2249 | 428250.6324 | 3323.2249
OfL-w09-v14-VRF_HP_OAU1 | OfL | CZ09 | 14 | VRF_HP_OAU1 | 654.3314 | 1753191.125 | 500422.4062 | 0 | 883691.5 | 2270.2422 | 272248.6562 | 0 | 213.4769 | 94346.1641 | 0 | 0 | 0 | 0 | 2848.4579 | 0 | 0 | 2848.4579 | 2864.0495 | 529160% | -551606% | 0% | 0% | 0% | 0% | 2864.0495 | 369078.5394 | 2864.0495
OfL-w09-v14-VRF_HP_OAU2 | OfL | CZ09 | 14 | VRF_HP_OAU2 | 616.5828 | 1720595.5 | 500422.4062 | 0 | 883691.5 | 2041.8013 | 239881.5312 | 0 | 213.4769 | 94346.1641 | 0 | 0 | 0 | 0 | 2848.4579 | 0 | 0 | 2848.4579 | 2611.1079 | 529160% | -551606% | 0% | 0% | 0% | 0% | 2611.1079 | 336482.9734 | 2611.1079
OfL-w09-v14-VRF_HR_OAU0 | OfL | CZ09 | 14 | VRF_HR_OAU0 | 697.2673 | 1783016.125 | 500422.4062 | 0 | 883691.5 | 2149.1428 | 301554.6562 | 0 | 213.4769 | 94985.625 | 0 | 0 | 0 | 0 | 2848.4291 | 0 | 0 | 2848.4291 | 3095.4865 | 534786% | -557517% | 0% | 0% | 0% | 0% | 3095.4865 | 398902.9009 | 3095.4865
OfL-w09-v14-VRF_HR_OAU1 | OfL | CZ09 | 14 | VRF_HR_OAU1 | 633.4772 | 1729189.625 | 500422.4062 | 0 | 883691.5 | 1818.9736 | 248058.5938 | 0 | 213.4769 | 94985.625 | 0 | 0 | 0 | 0 | 2848.4291 | 0 | 0 | 2848.4291 | 2677.795 | 534786% | -557517% | 0% | 0% | 0% | 0% | 2677.795 | 345076.6693 | 2677.795
OfL-w09-v14-VRF_HR_OAU2 | OfL | CZ09 | 14 | VRF_HR_OAU2 | 598.3779 | 1699684 | 500422.4062 | 0 | 883691.5 | 1631.0464 | 218741.4531 | 0 | 213.4769 | 94985.625 | 0 | 0 | 0 | 0 | 2848.4291 | 0 | 0 | 2848.4291 | 2448.8356 | 534786% | -557517% | 0% | 0% | 0% | 0% | 2448.8356 | 315571.6014 | 2448.8356
EPr-w09-v14-AC_S1Std | EPr | CZ09 | 14 | AC_S1Std | 229.6222 | 352479.625 | 133157.6562 | 0 | 99493.7734 | 0 | 49552.9375 | 0 | 0 | 70275.5156 | 0 | 0 | 0 | 0 | 6243.6845 | 110.3944 | 4035.2272 | 2098.063 | 1333.3915 | 217235% | -370461% | 0% | 0% | 0% | 0% | 1333.3915 | 119828.4531 | 929.8688
EPr-w09-v14-AC_S0Std | EPr | CZ09 | 14 | AC_S0Std | 229.6223 | 362552.0938 | 133157.6562 | 0 | 99493.7734 | 0 | 59625.4414 | 0 | 0 | 70275.5156 | 0 | 0 | 0 | 0 | 6243.3792 | 110.3944 | 4034.9226 | 2098.0624 | 1411.5237 | 217235% | -370461% | 0% | 0% | 0% | 0% | 1411.5237 | 129900.957 | 1008.0314
EPr-w09-v14-AC_SHi | EPr | CZ09 | 14 | AC_SHi | 192.2532 | 319663.8125 | 133157.6562 | 0 | 99493.7734 | 0 | 38482.6875 | 0 | 0 | 48530.0039 | 0 | 0 | 0 | 0 | 6339.3498 | 110.3944 | 4130.7277 | 2098.2269 | 1088.2913 | 212352% | -278924% | 0% | 0% | 0% | 0% | 1088.2913 | 87012.6914 | 675.2185
EPr-w09-v14-AC_EStd | EPr | CZ09 | 14 | AC_EStd | 245.2671 | 355047.4688 | 133157.6562 | 0 | 99493.7734 | 0 | 53536.1133 | 0 | 0 | 68860.0859 | 0 | 0 | 0 | 0 | 6072.1466 | 110.3944 | 3863.5501 | 2098.2034 | 1336.1495 | 225351% | -288157% | 0% | 0% | 0% | 0% | 1336.1495 | 122396.1992 | 949.7945
EPr-w09-v14-AC_EHi | EPr | CZ09 | 14 | AC_EHi | 220.076 | 345738.0938 | 133157.6562 | 0 | 99493.7734 | 0 | 44226.7656 | 0 | 0 | 68860.0859 | 0 | 0 | 0 | 0 | 6072.1466 | 110.3944 | 3863.5501 | 2098.2034 | 1263.909 | 225351% | -288157% | 0% | 0% | 0% | 0% | 1263.909 | 113086.8516 | 877.554
EPr-w09-v14-PVAV_Std | EPr | CZ09 | 14 | PVAV_Std | 241.8767 | 351132.2812 | 133157.6562 | 0 | 99493.7734 | 94.3271 | 65815.0469 | 0 | 184.3189 | 52387.2422 | 0 | 0 | 0 | 0 | 6461.4406 | 110.3944 | 4251.8867 | 2099.1584 | 1344.6007 | 226460% | -137475% | 0% | 0% | 0% | 0% | 1344.6007 | 118480.9351 | 919.4121
EPr-w09-v14-PVAV_Hi | EPr | CZ09 | 14 | PVAV_Hi | 205.5552 | 333979.75 | 133157.6562 | 0 | 99493.7734 | 168.5441 | 50857.5859 | 0 | 193.0439 | 50109.168 | 0 | 0 | 0 | 0 | 6334.3622 | 110.3944 | 4124.7856 | 2099.1813 | 1198.7865 | 222149% | -131156% | 0% | 0% | 0% | 0% | 1198.7865 | 101328.3419 | 786.3079
EPr-w09-v14-VRF_HP_OAU0 | EPr | CZ09 | 14 | VRF_HP_OAU0 | 226.7763 | 364528.625 | 133157.6562 | 0 | 99493.7734 | 21991.8672 | 54167.7617 | 0 | 0 | 55717.5781 | 0 | 0 | 0 | 0 | 2208.2019 | 110.3944 | 0 | 2097.807 | 1023.3671 | 190257% | -198260% | 0% | 0% | 0% | 0% | 1023.3671 | 131877.207 | 1023.3671
EPr-w09-v14-VRF_HP_OAU1 | EPr | CZ09 | 14 | VRF_HP_OAU1 | 210.7884 | 355941.625 | 133157.6562 | 0 | 99493.7734 | 19855.2461 | 47717.6055 | 0 | 0 | 55717.5781 | 0 | 0 | 0 | 0 | 2208.2019 | 110.3944 | 0 | 2097.807 | 956.7337 | 190257% | -198260% | 0% | 0% | 0% | 0% | 956.7337 | 123290.4297 | 956.7337
EPr-w09-v14-VRF_HP_OAU2 | EPr | CZ09 | 14 | VRF_HP_OAU2 | 197.3702 | 348645.0312 | 133157.6562 | 0 | 99493.7734 | 17976.2773 | 42300.0469 | 0 | 0 | 55717.5781 | 0 | 0 | 0 | 0 | 2208.2019 | 110.3944 | 0 | 2097.807 | 900.1127 | 190257% | -198260% | 0% | 0% | 0% | 0% | 900.1127 | 115993.9023 | 900.1127
EPr-w09-v14-VRF_HR_OAU0 | EPr | CZ09 | 14 | VRF_HR_OAU0 | 208.2677 | 355064.75 | 133157.6562 | 0 | 99493.7734 | 18647.0527 | 48454.4375 | 0 | 0 | 55311.9922 | 0 | 0 | 0 | 0 | 2208.1893 | 110.3944 | 0 | 2097.7946 | 949.9286 | 187198% | -195070% | 0% | 0% | 0% | 0% | 949.9286 | 122413.4824 | 949.9286
EPr-w09-v14-VRF_HR_OAU1 | EPr | CZ09 | 14 | VRF_HR_OAU1 | 194.5599 | 347404.9375 | 133157.6562 | 0 | 99493.7734 | 16751.4355 | 42690.2383 | 0 | 0 | 55311.9922 | 0 | 0 | 0 | 0 | 2208.1893 | 110.3944 | 0 | 2097.7946 | 890.4884 | 187198% | -195070% | 0% | 0% | 0% | 0% | 890.4884 | 114753.666 | 890.4884
EPr-w09-v14-VRF_HR_OAU2 | EPr | CZ09 | 14 | VRF_HR_OAU2 | 183.0398 | 340926.875 | 133157.6562 | 0 | 99493.7734 | 15119.7432 | 37843.9297 | 0 | 0 | 55311.9922 | 0 | 0 | 0 | 0 | 2208.1893 | 110.3944 | 0 | 2097.7946 | 840.2192 | 187198% | -195070% | 0% | 0% | 0% | 0% | 840.2192 | 108275.665 | 840.2192
Htl-w09-v14-FPFC_1 | Htl | CZ09 | 14 | FPFC_1 | 736.0905 | 4022720 | 566447.625 | 0 | 1692748 | 6468.1304 | 844013.9375 | 12180.416 | 392475.2812 | 508385.2188 | 0 | 0 | 0 | 0 | 119326.8122 | 0 | 83102.0749 | 36224.7347 | 21900.6258 | 827936% | -1433729% | 0% | 0% | 0% | 0% | 21900.6258 | 1751342.5679 | 13590.4183
Htl-w09-v14-FPFC_2 | Htl | CZ09 | 14 | FPFC_2 | 682.8291 | 3796908.75 | 566447.625 | 0 | 1692748 | 16294.2227 | 579675.4375 | 40417.9297 | 392680.8438 | 508644.0625 | 0 | 0 | 0 | 0 | 103238.615 | 0 | 67013.9494 | 36224.6758 | 18320.4008 | 827936% | -1433729% | 0% | 0% | 0% | 0% | 18320.4008 | 1497294.5664 | 11619.0058
Htl-w09-v14-VRF_HP_OAU0 | Htl | CZ09 | 14 | VRF_HP_OAU0 | 960.8306 | 3819061 | 566447.625 | 0 | 1692748 | 446970.5625 | 640474.625 | 0 | 1121.6216 | 471298.5 | 0 | 0 | 0 | 0 | 36224.4326 | 0 | 0 | 36224.4326 | 12104.5548 | 843520% | -873698% | 19.4% | 0% | 1700% | 0% | 12104.5548 | 1559865.3091 | 12104.5548
Htl-w09-v14-VRF_HP_OAU1 | Htl | CZ09 | 14 | VRF_HP_OAU1 | 873.3163 | 3675679 | 566447.625 | 0 | 1692748 | 398710.1562 | 545352.6875 | 0 | 1121.6216 | 471298.5 | 0 | 0 | 0 | 0 | 36224.4326 | 0 | 0 | 36224.4326 | 10991.9078 | 843520% | -873698% | 19.4% | 0% | 1700% | 0% | 10991.9078 | 1416482.9653 | 10991.9078
Htl-w09-v14-VRF_HP_OAU2 | Htl | CZ09 | 14 | VRF_HP_OAU2 | 807.2155 | 3565062.25 | 566447.625 | 0 | 1692748 | 358698.3125 | 474747 | 0 | 1121.6216 | 471298.5 | 0 | 0 | 0 | 0 | 36224.4326 | 0 | 0 | 36224.4326 | 10133.5158 | 843520% | -873698% | 19.4% | 0% | 1700% | 0% | 10133.5158 | 1305865.4341 | 10133.5158
Htl-w09-v14-VRF_HR_OAU0 | Htl | CZ09 | 14 | VRF_HR_OAU0 | 925.9567 | 3740948.25 | 566447.625 | 0 | 1692748 | 400741.9688 | 610030.3125 | 0 | 1121.6216 | 469857.9688 | 0 | 0 | 0 | 0 | 36224.3533 | 0 | 0 | 36224.3533 | 11498.3945 | 838569% | -868447% | 91.31% | 0% | 7700% | 300% | 11498.3945 | 1481751.8716 | 11498.3945
Htl-w09-v14-VRF_HR_OAU1 | Htl | CZ09 | 14 | VRF_HR_OAU1 | 843.2548 | 3604181.25 | 566447.625 | 0 | 1692748 | 355246.875 | 518757.5625 | 0 | 1121.6216 | 469857.9688 | 0 | 0 | 0 | 0 | 36224.3533 | 0 | 0 | 36224.3533 | 10437.0761 | 838569% | -868447% | 91.31% | 0% | 7700% | 300% | 10437.0761 | 1344984.0278 | 10437.0761
Htl-w09-v14-VRF_HR_OAU2 | Htl | CZ09 | 14 | VRF_HR_OAU2 | 780.8423 | 3499637.5 | 566447.625 | 0 | 1692748 | 318066.0312 | 451396.2188 | 0 | 1121.6216 | 469857.9688 | 0 | 0 | 0 | 0 | 36224.3533 | 0 | 0 | 36224.3533 | 9625.8287 | 838569% | -868447% | 91.31% | 0% | 7700% | 300% | 9625.8287 | 1240441.8403 | 9625.8287
OfS-w10-v14-AC_S1Std | OfS | CZ10 | 14 | AC_S1Std | 44.6954 | 108107.6094 | 31593.9805 | 0 | 50648.0078 | 0 | 15922.8877 | 0 | 0 | 9942.8945 | 0 | 0 | 0 | 0 | 218.7719 | 0 | 48.0881 | 170.6838 | 205.5273 | 29482% | -38858% | 0% | 0% | 0% | 0% | 205.5273 | 25865.7822 | 200.7185
OfS-w10-v14-AC_S0Std | OfS | CZ10 | 14 | AC_S0Std | 44.6956 | 112252.625 | 31593.9805 | 0 | 50648.0078 | 0 | 20068.3066 | 0 | 0 | 9942.4863 | 0 | 0 | 0 | 0 | 218.6974 | 0 | 48.0145 | 170.6829 | 237.6852 | 29483% | -38856% | 0% | 0% | 0% | 0% | 237.6852 | 30010.793 | 232.8838
OfS-w10-v14-AC_SHi | OfS | CZ10 | 14 | AC_SHi | 40 | 100002.0938 | 31593.9805 | 0 | 50648.0078 | 0 | 12577.3438 | 0 | 0 | 5182.8843 | 0 | 0 | 0 | 0 | 229.3626 | 0 | 58.6105 | 170.7522 | 143.6804 | 29826% | -33335% | 0% | 0% | 0% | 0% | 143.6804 | 17760.228 | 137.8194
OfS-w10-v14-AC_EStd | OfS | CZ10 | 14 | AC_EStd | 47.0328 | 107278.9219 | 31593.9805 | 0 | 50648.0078 | 0 | 16895.709 | 0 | 0 | 8141.3438 | 0 | 0 | 0 | 0 | 222.9224 | 0 | 52.1872 | 170.7353 | 199.5062 | 29627% | -32948% | 0% | 0% | 0% | 0% | 199.5062 | 25037.0527 | 194.2875
OfS-w10-v14-AC_EHi | OfS | CZ10 | 14 | AC_EHi | 42.9885 | 104340.9219 | 31593.9805 | 0 | 50648.0078 | 0 | 13957.7197 | 0 | 0 | 8141.3438 | 0 | 0 | 0 | 0 | 222.9224 | 0 | 52.1872 | 170.7353 | 176.7074 | 29627% | -32948% | 0% | 0% | 0% | 0% | 176.7074 | 22099.0635 | 171.4887
OfS-w10-v14-PVAV_Std | OfS | CZ10 | 14 | PVAV_Std | 49.6661 | 110258.125 | 31593.9805 | 0 | 50648.0078 | 7.5669 | 22598.8379 | 0 | 150.2335 | 5259.5859 | 0 | 0 | 0 | 0 | 274.7725 | 0 | 103.9317 | 170.8408 | 227.7991 | 0% | 0% | 0% | 0% | 0% | 0% | 227.7991 | 28016.2242 | 217.4059
OfS-w10-v14-PVAV_Hi | OfS | CZ10 | 14 | PVAV_Hi | 43.1052 | 104816.4062 | 31593.9805 | 0 | 50648.0078 | 13.6684 | 17099.2871 | 0 | 150.2883 | 5311.248 | 0 | 0 | 0 | 0 | 236.9125 | 0 | 66.0764 | 170.8361 | 181.7857 | 0% | 0% | 0% | 0% | 0% | 0% | 181.7857 | 22574.4919 | 175.1781
OfS-w10-v14-VRF_HP_OAU0 | OfS | CZ10 | 14 | VRF_HP_OAU0 | 45.5965 | 106994.4062 | 31593.9805 | 0 | 50648.0078 | 577.6074 | 19088.4121 | 0 | 0 | 5086.5303 | 0 | 0 | 0 | 0 | 170.6959 | 0 | 0 | 170.6959 | 192.0798 | 29007% | -30235% | 0% | 0% | 0% | 0% | 192.0798 | 24752.5498 | 192.0798
OfS-w10-v14-VRF_HP_OAU1 | OfS | CZ10 | 14 | VRF_HP_OAU1 | 42.7461 | 104666.875 | 31593.9805 | 0 | 50648.0078 | 521.3123 | 16817.1582 | 0 | 0 | 5086.5303 | 0 | 0 | 0 | 0 | 170.6959 | 0 | 0 | 170.6959 | 174.018 | 29007% | -30235% | 0% | 0% | 0% | 0% | 174.018 | 22425.0007 | 174.018
OfS-w10-v14-VRF_HP_OAU2 | OfS | CZ10 | 14 | VRF_HP_OAU2 | 40.3598 | 102705.25 | 31593.9805 | 0 | 50648.0078 | 471.5565 | 14905.3086 | 0 | 0 | 5086.5303 | 0 | 0 | 0 | 0 | 170.6959 | 0 | 0 | 170.6959 | 158.7959 | 29007% | -30235% | 0% | 0% | 0% | 0% | 158.7959 | 20463.3953 | 158.7959
OfS-w10-v14-VRF_HR_OAU0 | OfS | CZ10 | 14 | VRF_HR_OAU0 | 44.9341 | 105516.7188 | 31593.9805 | 0 | 50648.0078 | 474.4633 | 17708.3203 | 0 | 0 | 5092.0645 | 0 | 0 | 0 | 0 | 170.6744 | 0 | 0 | 170.6744 | 180.6128 | 29006% | -30236% | 0% | 0% | 0% | 0% | 180.6128 | 23274.8481 | 180.6128
OfS-w10-v14-VRF_HR_OAU1 | OfS | CZ10 | 14 | VRF_HR_OAU1 | 42.1703 | 103355.7266 | 31593.9805 | 0 | 50648.0078 | 425.6846 | 15596.085 | 0 | 0 | 5092.0645 | 0 | 0 | 0 | 0 | 170.6744 | 0 | 0 | 170.6744 | 163.8434 | 29006% | -30236% | 0% | 0% | 0% | 0% | 163.8434 | 21113.834 | 163.8434
OfS-w10-v14-VRF_HR_OAU2 | OfS | CZ10 | 14 | VRF_HR_OAU2 | 39.8555 | 101539.4219 | 31593.9805 | 0 | 50648.0078 | 383.2244 | 13822.2461 | 0 | 0 | 5092.0645 | 0 | 0 | 0 | 0 | 170.6744 | 0 | 0 | 170.6744 | 149.7489 | 29006% | -30236% | 0% | 0% | 0% | 0% | 149.7489 | 19297.535 | 149.7489
OfL-w10-v14-FPFC_1 | OfL | CZ10 | 14 | FPFC_1 | 541.8077 | 1851987 | 500422.4062 | 0 | 883691.5 | 179.0577 | 294034.9688 | 5984.5093 | 90321.2266 | 77353.9609 | 0 | 0 | 0 | 0 | 5118.8966 | 0 | 2283.0091 | 2835.8867 | 3812.5612 | 434109% | -807854% | 0% | 0% | 0% | 0% | 3812.5612 | 461889.214 | 3584.2603
OfL-w10-v14-FPFC_2 | OfL | CZ10 | 14 | FPFC_2 | 513.4553 | 1783293.625 | 500422.4062 | 0 | 883691.5 | 356.1307 | 217931.2656 | 13342.7734 | 90200.375 | 77350.4297 | 0 | 0 | 0 | 0 | 3954.6509 | 0 | 1118.744 | 2835.9066 | 3105.9788 | 434109% | -807854% | 0% | 0% | 0% | 0% | 3105.9788 | 385838.201 | 2994.1044
OfL-w10-v14-VRF_HP_OAU0 | OfL | CZ10 | 14 | VRF_HP_OAU0 | 738.1511 | 1825547.5 | 500422.4062 | 0 | 883691.5 | 3504.8416 | 347007.7188 | 0 | 213.4769 | 90708.4766 | 0 | 0 | 0 | 0 | 2835.3149 | 0 | 0 | 2835.3149 | 3425.5318 | 495736% | -516302% | 0% | 0% | 0% | 0% | 3425.5318 | 441434.5137 | 3425.5318
OfL-w10-v14-VRF_HP_OAU1 | OfL | CZ10 | 14 | VRF_HP_OAU1 | 666.1469 | 1763459.875 | 500422.4062 | 0 | 883691.5 | 2998.0845 | 285426.9062 | 0 | 213.4769 | 90708.4766 | 0 | 0 | 0 | 0 | 2835.3149 | 0 | 0 | 2835.3149 | 2943.7323 | 495736% | -516302% | 0% | 0% | 0% | 0% | 2943.7323 | 379346.9442 | 2943.7323
OfL-w10-v14-VRF_HP_OAU2 | OfL | CZ10 | 14 | VRF_HP_OAU2 | 626.6702 | 1729282 | 500422.4062 | 0 | 883691.5 | 2703.1733 | 251544.375 | 0 | 213.4769 | 90708.4766 | 0 | 0 | 0 | 0 | 2835.3149 | 0 | 0 | 2835.3149 | 2678.5153 | 495736% | -516302% | 0% | 0% | 0% | 0% | 2678.5153 | 345169.5018 | 2678.5153
OfL-w10-v14-VRF_HR_OAU0 | OfL | CZ10 | 14 | VRF_HR_OAU0 | 750.4159 | 1804381.875 | 500422.4062 | 0 | 883691.5 | 2876.7776 | 325323.0625 | 0 | 213.4769 | 91855.5078 | 0 | 0 | 0 | 0 | 2835.288 | 0 | 0 | 2835.288 | 3261.2861 | 505711% | -526563% | 0% | 0% | 0% | 0% | 3261.2861 | 420268.8248 | 3261.2861
OfL-w10-v14-VRF_HR_OAU1 | OfL | CZ10 | 14 | VRF_HR_OAU1 | 675.9462 | 1746165.25 | 500422.4062 | 0 | 883691.5 | 2441.5625 | 267541.9375 | 0 | 213.4769 | 91855.5078 | 0 | 0 | 0 | 0 | 2835.288 | 0 | 0 | 2835.288 | 2809.5273 | 505711% | -526563% | 0% | 0% | 0% | 0% | 2809.5273 | 362052.4847 | 2809.5273
OfL-w10-v14-VRF_HR_OAU2 | OfL | CZ10 | 14 | VRF_HR_OAU2 | 635.1567 | 1714238.25 | 500422.4062 | 0 | 883691.5 | 2188.9819 | 235867.7188 | 0 | 213.4769 | 91855.5078 | 0 | 0 | 0 | 0 | 2835.288 | 0 | 0 | 2835.288 | 2561.7753 | 505711% | -526563% | 0% | 0% | 0% | 0% | 2561.7753 | 330125.6854 | 2561.7753
EPr-w10-v14-AC_S1Std | EPr | CZ10 | 14 | AC_S1Std | 228.764 | 350260.3125 | 133157.6562 | 0 | 99493.7734 | 0 | 56459.1172 | 0 | 0 | 61150.125 | 0 | 0 | 0 | 0 | 6398.752 | 110.3944 | 4197.2547 | 2091.103 | 1332.3732 | 181514% | -335547% | 22.93% | 0% | 600% | 0% | 1332.3732 | 117609.2422 | 912.6477
EPr-w10-v14-AC_S0Std | EPr | CZ10 | 14 | AC_S0Std | 228.7642 | 357811.5 | 133157.6562 | 0 | 99493.7734 | 0 | 64010.25 | 0 | 0 | 61150.1328 | 0 | 0 | 0 | 0 | 6398.585 | 110.3944 | 4197.0883 | 2091.1027 | 1390.9534 | 181514% | -335547% | 22.93% | 0% | 600% | 0% | 1390.9534 | 125160.3828 | 971.2446
EPr-w10-v14-AC_SHi | EPr | CZ10 | 14 | AC_SHi | 197.7381 | 321169.9688 | 133157.6562 | 0 | 99493.7734 | 0 | 44516.8828 | 0 | 0 | 44001.8984 | 0 | 0 | 0 | 0 | 6494.9683 | 110.3944 | 4293.3171 | 2091.2565 | 1116.2375 | 179330% | -277345% | 22.93% | 0% | 600% | 0% | 1116.2375 | 88518.7812 | 686.9057
EPr-w10-v14-AC_EStd | EPr | CZ10 | 14 | AC_EStd | 249.5345 | 355116.4375 | 133157.6562 | 0 | 99493.7734 | 0 | 61258.7578 | 0 | 0 | 61206.5078 | 0 | 0 | 0 | 0 | 6280.5331 | 110.3944 | 4078.9082 | 2091.2298 | 1358.2213 | 185714% | -284382% | 30.57% | 0% | 800% | 0% | 1358.2213 | 122465.2656 | 950.3305
EPr-w10-v14-AC_EHi | EPr | CZ10 | 14 | AC_EHi | 223.4107 | 344464.0938 | 133157.6562 | 0 | 99493.7734 | 0 | 50606.5117 | 0 | 0 | 61206.5078 | 0 | 0 | 0 | 0 | 6280.5331 | 110.3944 | 4078.9082 | 2091.2298 | 1275.5598 | 185714% | -284382% | 30.57% | 0% | 800% | 0% | 1275.5598 | 111813.0195 | 867.669
EPr-w10-v14-PVAV_Std | EPr | CZ10 | 14 | PVAV_Std | 241.9881 | 354238.3438 | 133157.6562 | 0 | 99493.7734 | 103.9171 | 72765.2188 | 0 | 230.2036 | 48487.6406 | 0 | 0 | 0 | 0 | 6630.5235 | 110.3944 | 4427.9718 | 2092.159 | 1386.3121 | 188743% | -130426% | 19.11% | 0% | 500% | 0% | 1386.3121 | 121586.9801 | 943.515
EPr-w10-v14-PVAV_Hi | EPr | CZ10 | 14 | PVAV_Hi | 205.3067 | 336033.1875 | 133157.6562 | 0 | 99493.7734 | 185.5756 | 56179.8945 | 0 | 238.9843 | 46777.3125 | 0 | 0 | 0 | 0 | 6447.9808 | 110.3944 | 4245.3952 | 2092.1906 | 1226.782 | 187303% | -126073% | 7.642% | 0% | 200% | 0% | 1226.782 | 103381.767 | 802.2425
EPr-w10-v14-VRF_HP_OAU0 | EPr | CZ10 | 14 | VRF_HP_OAU0 | 253.1601 | 368788.875 | 133157.6562 | 0 | 99493.7734 | 22990.5352 | 61231.9492 | 0 | 0 | 51915.0234 | 0 | 0 | 0 | 0 | 2201.1917 | 110.3944 | 0 | 2090.7973 | 1056.4271 | 150906% | -157176% | 3.821% | 0% | 100% | 0% | 1056.4271 | 136137.5078 | 1056.4271
EPr-w10-v14-VRF_HP_OAU1 | EPr | CZ10 | 14 | VRF_HP_OAU1 | 233.2884 | 359285.0625 | 133157.6562 | 0 | 99493.7734 | 20778.2305 | 53940.6836 | 0 | 0 | 51915.0195 | 0 | 0 | 0 | 0 | 2201.1917 | 110.3944 | 0 | 2090.7973 | 982.6793 | 150906% | -157176% | 3.821% | 0% | 100% | 0% | 982.6793 | 126633.9336 | 982.6793
EPr-w10-v14-VRF_HP_OAU2 | EPr | CZ10 | 14 | VRF_HP_OAU2 | 216.5591 | 351214.1562 | 133157.6562 | 0 | 99493.7734 | 18832.375 | 47815.6602 | 0 | 0 | 51915.0273 | 0 | 0 | 0 | 0 | 2201.1917 | 110.3944 | 0 | 2090.7973 | 920.0494 | 150906% | -157176% | 3.821% | 0% | 100% | 0% | 920.0494 | 118563.0625 | 920.0494
EPr-w10-v14-VRF_HR_OAU0 | EPr | CZ10 | 14 | VRF_HR_OAU0 | 240.8104 | 359537.4062 | 133157.6562 | 0 | 99493.7734 | 19487.5391 | 55597.6914 | 0 | 0 | 51800.9453 | 0 | 0 | 0 | 0 | 2201.1805 | 110.3944 | 0 | 2090.7856 | 984.6367 | 149920% | -156022% | 7.642% | 0% | 200% | 0% | 984.6367 | 126886.1758 | 984.6367
EPr-w10-v14-VRF_HR_OAU1 | EPr | CZ10 | 14 | VRF_HR_OAU1 | 222.5002 | 351004.0312 | 133157.6562 | 0 | 99493.7734 | 17557.2988 | 48994.5352 | 0 | 0 | 51800.9453 | 0 | 0 | 0 | 0 | 2201.1805 | 110.3944 | 0 | 2090.7856 | 918.4176 | 149920% | -156022% | 3.821% | 0% | 100% | 0% | 918.4176 | 118352.7793 | 918.4176
EPr-w10-v14-VRF_HR_OAU2 | EPr | CZ10 | 14 | VRF_HR_OAU2 | 207.3084 | 343753.375 | 133157.6562 | 0 | 99493.7734 | 15842.8516 | 43458.25 | 0 | 0 | 51800.9453 | 0 | 0 | 0 | 0 | 2201.1805 | 110.3944 | 0 | 2090.7856 | 862.1519 | 149920% | -156022% | 3.821% | 0% | 100% | 0% | 862.1519 | 111102.0469 | 862.1519
Htl-w10-v14-FPFC_1 | Htl | CZ10 | 14 | FPFC_1 | 747.2887 | 4010517 | 566447.625 | 0 | 1692748 | 7322.7773 | 788538.375 | 14077.292 | 344414.1875 | 596968.625 | 0 | 0 | 0 | 0 | 129477.2531 | 0 | 93483.4278 | 35993.8611 | 22829.356 | 919937% | -1738427% | 9.131% | 0% | 800% | 0% | 22829.356 | 1737243.9648 | 13481.0132
Htl-w10-v14-FPFC_2 | Htl | CZ10 | 14 | FPFC_2 | 694.0917 | 3821768.75 | 566447.625 | 0 | 1692748 | 19902.8047 | 564724.625 | 35832.8008 | 344654.7812 | 597456.875 | 0 | 0 | 0 | 0 | 109736.0794 | 0 | 73742.249 | 35993.8227 | 19221.7202 | 919937% | -1738427% | 9.131% | 0% | 800% | 0% | 19221.7202 | 1526739.0859 | 11847.4953
Htl-w10-v14-VRF_HP_OAU0 | Htl | CZ10 | 14 | VRF_HP_OAU0 | 1076.2277 | 3956137.5 | 566447.625 | 0 | 1692748 | 508595.75 | 726736.6875 | 0 | 1121.6216 | 460487.2188 | 0 | 0 | 0 | 0 | 35993.7075 | 0 | 0 | 35993.7075 | 13168.2643 | 811103% | -839331% | 23.97% | 0% | 2100% | 0% | 13168.2643 | 1696941.2778 | 13168.2643
Htl-w10-v14-VRF_HP_OAU1 | Htl | CZ10 | 14 | VRF_HP_OAU1 | 967.8876 | 3795329.5 | 566447.625 | 0 | 1692748 | 454253.0312 | 620270.6875 | 0 | 1121.6216 | 460487.2812 | 0 | 0 | 0 | 0 | 35993.7075 | 0 | 0 | 35993.7075 | 11920.3891 | 811104% | -839332% | 23.97% | 0% | 2100% | 0% | 11920.3891 | 1536132.6216 | 11920.3891
Htl-w10-v14-VRF_HP_OAU2 | Htl | CZ10 | 14 | VRF_HP_OAU2 | 886.3603 | 3670392.5 | 566447.625 | 0 | 1692748 | 408923.9062 | 540663.625 | 0 | 1121.6216 | 460487.2812 | 0 | 0 | 0 | 0 | 35993.7075 | 0 | 0 | 35993.7075 | 10950.8843 | 811104% | -839332% | 23.97% | 0% | 2100% | 0% | 10950.8843 | 1411196.4341 | 10950.8843
Htl-w10-v14-VRF_HR_OAU0 | Htl | CZ10 | 14 | VRF_HR_OAU0 | 1041.4476 | 3866708 | 566447.625 | 0 | 1692748 | 457265.875 | 689494.875 | 0 | 1121.6216 | 459629.1562 | 0 | 0 | 0 | 0 | 35993.6102 | 0 | 0 | 35993.6102 | 12474.2895 | 807887% | -835863% | 97.02% | 0% | 8500% | 0% | 12474.2895 | 1607511.5278 | 12474.2895
Htl-w10-v14-VRF_HR_OAU1 | Htl | CZ10 | 14 | VRF_HR_OAU1 | 939.3483 | 3713750.5 | 566447.625 | 0 | 1692748 | 406514.3125 | 587288.8125 | 0 | 1121.6216 | 459629.1562 | 0 | 0 | 0 | 0 | 35993.6102 | 0 | 0 | 35993.6102 | 11287.3383 | 807887% | -835863% | 97.02% | 0% | 8500% | 0% | 11287.3383 | 1454553.9028 | 11287.3383
Htl-w10-v14-VRF_HR_OAU2 | Htl | CZ10 | 14 | VRF_HR_OAU2 | 862.931 | 3596485.75 | 566447.625 | 0 | 1692748 | 364810.9688 | 511726.875 | 0 | 1121.6216 | 459629.1562 | 0 | 0 | 0 | 0 | 35993.6102 | 0 | 0 | 35993.6102 | 10377.3597 | 807887% | -835863% | 97.02% | 0% | 8500% | 0% | 10377.3597 | 1337288.6216 | 10377.3597
OfS-w11-v14-AC_S1Std | OfS | CZ11 | 14 | AC_S1Std | 44.5263 | 109339.0859 | 31593.9805 | 0 | 50648.0078 | 0 | 16481.1855 | 0 | 0 | 10616.0527 | 0 | 0 | 0 | 0 | 434.3782 | 0 | 261.5185 | 172.8598 | 236.4264 | 31121% | -42291% | 0% | 0% | 0% | 0% | 236.4264 | 27097.2383 | 210.2746
OfS-w11-v14-AC_S0Std | OfS | CZ11 | 14 | AC_S0Std | 44.5271 | 112625.7266 | 31593.9805 | 0 | 50648.0078 | 0 | 19767.8887 | 0 | 0 | 10615.9287 | 0 | 0 | 0 | 0 | 434.2455 | 0 | 261.3865 | 172.8589 | 261.9171 | 31122% | -42291% | 0% | 0% | 0% | 0% | 261.9171 | 30383.8174 | 235.7784
OfS-w11-v14-AC_SHi | OfS | CZ11 | 14 | AC_SHi | 39.5183 | 100674.0547 | 31593.9805 | 0 | 50648.0078 | 0 | 12943.7119 | 0 | 0 | 5488.4629 | 0 | 0 | 0 | 0 | 472.8694 | 0 | 299.9369 | 172.9324 | 173.0274 | 31529% | -36599% | 0% | 0% | 0% | 0% | 173.0274 | 18432.1748 | 143.0337
OfS-w11-v14-AC_EStd | OfS | CZ11 | 14 | AC_EStd | 46.439 | 108176.7188 | 31593.9805 | 0 | 50648.0078 | 0 | 17356.6289 | 0 | 0 | 8578.1914 | 0 | 0 | 0 | 0 | 451.4963 | 0 | 278.5824 | 172.914 | 229.1124 | 31201% | -36178% | 0% | 0% | 0% | 0% | 229.1124 | 25934.8203 | 201.2542
OfS-w11-v14-AC_EHi | OfS | CZ11 | 14 | AC_EHi | 42.4738 | 105158.5781 | 31593.9805 | 0 | 50648.0078 | 0 | 14338.498 | 0 | 0 | 8578.1914 | 0 | 0 | 0 | 0 | 451.4963 | 0 | 278.5824 | 172.914 | 205.6917 | 31201% | -36178% | 0% | 0% | 0% | 0% | 205.6917 | 22916.6895 | 177.8335
OfS-w11-v14-PVAV_Std | OfS | CZ11 | 14 | PVAV_Std | 47.931 | 109924.5234 | 31593.9805 | 0 | 50648.0078 | 24.6231 | 21991.8281 | 0 | 287.2408 | 5378.9043 | 0 | 0 | 0 | 0 | 516.7021 | 0 | 343.7807 | 172.9213 | 249.195 | 0% | 0% | 0% | 0% | 0% | 0% | 249.195 | 27682.5963 | 214.8169
OfS-w11-v14-PVAV_Hi | OfS | CZ11 | 14 | PVAV_Hi | 41.8133 | 104619.1875 | 31593.9805 | 0 | 50648.0078 | 46.504 | 16638.3555 | 0 | 288.6846 | 5403.7153 | 0 | 0 | 0 | 0 | 419.4282 | 0 | 246.5051 | 172.9231 | 198.298 | 0% | 0% | 0% | 0% | 0% | 0% | 198.298 | 22377.2594 | 173.6475
OfS-w11-v14-VRF_HP_OAU0 | OfS | CZ11 | 14 | VRF_HP_OAU0 | 43.952 | 108806.875 | 31593.9805 | 0 | 50648.0078 | 2416.4893 | 18965.5938 | 0 | 0 | 5182.9189 | 0 | 0 | 0 | 0 | 172.824 | 0 | 0 | 172.824 | 206.1444 | 29193% | -30491% | 0% | 0% | 0% | 0% | 206.1444 | 26565.002 | 206.1444
OfS-w11-v14-VRF_HP_OAU1 | OfS | CZ11 | 14 | VRF_HP_OAU1 | 41.303 | 106331.9531 | 31593.9805 | 0 | 50648.0078 | 2186.2351 | 16720.9199 | 0 | 0 | 5182.9189 | 0 | 0 | 0 | 0 | 172.824 | 0 | 0 | 172.824 | 186.939 | 29193% | -30491% | 0% | 0% | 0% | 0% | 186.939 | 24090.074 | 186.939
OfS-w11-v14-VRF_HP_OAU2 | OfS | CZ11 | 14 | VRF_HP_OAU2 | 39.035 | 104232.9297 | 31593.9805 | 0 | 50648.0078 | 1983.4587 | 14824.71 | 0 | 0 | 5182.9189 | 0 | 0 | 0 | 0 | 172.824 | 0 | 0 | 172.824 | 170.6508 | 29193% | -30491% | 0% | 0% | 0% | 0% | 170.6508 | 21991.0876 | 170.6508
OfS-w11-v14-VRF_HR_OAU0 | OfS | CZ11 | 14 | VRF_HR_OAU0 | 43.2172 | 107319.6562 | 31593.9805 | 0 | 50648.0078 | 2030.7018 | 17859.1641 | 0 | 0 | 5187.918 | 0 | 0 | 0 | 0 | 172.8072 | 0 | 0 | 172.8072 | 194.6036 | 29007% | -30298% | 0% | 0% | 0% | 0% | 194.6036 | 25077.7838 | 194.6036
OfS-w11-v14-VRF_HR_OAU1 | OfS | CZ11 | 14 | VRF_HR_OAU1 | 40.6611 | 104995.5781 | 31593.9805 | 0 | 50648.0078 | 1826.475 | 15739.3164 | 0 | 0 | 5187.918 | 0 | 0 | 0 | 0 | 172.8072 | 0 | 0 | 172.8072 | 176.5688 | 29007% | -30298% | 0% | 0% | 0% | 0% | 176.5688 | 22753.7094 | 176.5688
OfS-w11-v14-VRF_HR_OAU2 | OfS | CZ11 | 14 | VRF_HR_OAU2 | 38.5192 | 103029.3906 | 31593.9805 | 0 | 50648.0078 | 1648.9993 | 13950.5986 | 0 | 0 | 5187.918 | 0 | 0 | 0 | 0 | 172.8072 | 0 | 0 | 172.8072 | 161.3111 | 29007% | -30298% | 0% | 0% | 0% | 0% | 161.3111 | 20787.5159 | 161.3111
OfL-w11-v14-FPFC_1 | OfL | CZ11 | 14 | FPFC_1 | 527.7437 | 1842696.5 | 500422.4062 | 0 | 883691.5 | 401.2473 | 279394.7188 | 5795.9243 | 92031.375 | 80960.2891 | 0 | 0 | 0 | 0 | 8008.0538 | 0 | 5134.921 | 2873.1315 | 4027.1241 | 456359% | -887607% | 0% | 0% | 0% | 0% | 4027.1241 | 452787.6301 | 3513.632
OfL-w11-v14-FPFC_2 | OfL | CZ11 | 14 | FPFC_2 | 496.7815 | 1776374.375 | 500422.4062 | 0 | 883691.5 | 895.7625 | 206571.2344 | 12262.7812 | 91575.0625 | 80956.8828 | 0 | 0 | 0 | 0 | 5890.3283 | 0 | 3017.1558 | 2873.1715 | 3250.5074 | 456359% | -887607% | 0% | 0% | 0% | 0% | 3250.5074 | 379998.9421 | 2948.7918
OfL-w11-v14-VRF_HP_OAU0 | OfL | CZ11 | 14 | VRF_HP_OAU0 | 693.4312 | 1820022.75 | 500422.4062 | 0 | 883691.5 | 15663.0898 | 330187.3125 | 0 | 213.4769 | 89846.3281 | 0 | 0 | 0 | 0 | 2872.6659 | 0 | 0 | 2872.6659 | 3382.6632 | 484627% | -506287% | 0% | 0% | 0% | 0% | 3382.6632 | 435910.2073 | 3382.6632
OfL-w11-v14-VRF_HP_OAU1 | OfL | CZ11 | 14 | VRF_HP_OAU1 | 629.5374 | 1759258.375 | 500422.4062 | 0 | 883691.5 | 13453.4863 | 271632.625 | 0 | 213.4769 | 89846.3281 | 0 | 0 | 0 | 0 | 2872.6659 | 0 | 0 | 2872.6659 | 2911.1323 | 484627% | -506287% | 0% | 0% | 0% | 0% | 2911.1323 | 375145.9163 | 2911.1323
OfL-w11-v14-VRF_HP_OAU2 | OfL | CZ11 | 14 | VRF_HP_OAU2 | 594.394 | 1725780.75 | 500422.4062 | 0 | 883691.5 | 12160.8242 | 239447.9062 | 0 | 213.4769 | 89846.3047 | 0 | 0 | 0 | 0 | 2872.6659 | 0 | 0 | 2872.6659 | 2651.3477 | 484627% | -506287% | 0% | 0% | 0% | 0% | 2651.3477 | 341668.512 | 2651.3477
OfL-w11-v14-VRF_HR_OAU0 | OfL | CZ11 | 14 | VRF_HR_OAU0 | 694.1595 | 1805504.375 | 500422.4062 | 0 | 883691.5 | 13128.5127 | 317759.625 | 0 | 213.4769 | 90289.9688 | 0 | 0 | 0 | 0 | 2872.6448 | 0 | 0 | 2872.6448 | 3269.9987 | 485399% | -507013% | 0% | 0% | 0% | 0% | 3269.9987 | 421391.5833 | 3269.9987
OfL-w11-v14-VRF_HR_OAU1 | OfL | CZ11 | 14 | VRF_HR_OAU1 | 630.1627 | 1747130.125 | 500422.4062 | 0 | 883691.5 | 11205.0312 | 261309.2344 | 0 | 213.4769 | 90289.9297 | 0 | 0 | 0 | 0 | 2872.6448 | 0 | 0 | 2872.6448 | 2817.0171 | 485399% | -507013% | 0% | 0% | 0% | 0% | 2817.0171 | 363017.6722 | 2817.0171
OfL-w11-v14-VRF_HR_OAU2 | OfL | CZ11 | 14 | VRF_HR_OAU2 | 595.0364 | 1715311 | 500422.4062 | 0 | 883691.5 | 10063.2256 | 230632.0781 | 0 | 213.4769 | 90289.9297 | 0 | 0 | 0 | 0 | 2872.6448 | 0 | 0 | 2872.6448 | 2570.102 | 485399% | -507013% | 0% | 0% | 0% | 0% | 2570.102 | 331198.7103 | 2570.102
EPr-w11-v14-AC_S1Std | EPr | CZ11 | 14 | AC_S1Std | 16.2798 | 346332.3125 | 133157.6562 | 0 | 99493.7734 | 0 | 52929.8828 | 0 | 0 | 60751.5117 | 0 | 0 | 0 | 0 | 10400.3955 | 110.3944 | 8157.4829 | 2132.5197 | 1697.9159 | 178257% | -360676% | 0% | 0% | 0% | 0% | 1697.9159 | 113681.3945 | 882.1676
EPr-w11-v14-AC_S0Std | EPr | CZ11 | 14 | AC_S0Std | 16.2798 | 351149.5312 | 133157.6562 | 0 | 99493.7734 | 0 | 57746.7969 | 0 | 0 | 60751.7578 | 0 | 0 | 0 | 0 | 10400.2701 | 110.3944 | 8157.3587 | 2132.5192 | 1735.2847 | 178257% | -360676% | 0% | 0% | 0% | 0% | 1735.2847 | 118498.5547 | 919.5488
EPr-w11-v14-AC_SHi | EPr | CZ11 | 14 | AC_SHi | 13.7919 | 318098.5 | 133157.6562 | 0 | 99493.7734 | 0 | 41619.5039 | 0 | 0 | 43827.7422 | 0 | 0 | 0 | 0 | 10525.3107 | 110.3944 | 8282.2406 | 2132.6768 | 1491.2947 | 177985% | -301570% | 0% | 0% | 0% | 0% | 1491.2947 | 85447.2461 | 663.0706
EPr-w11-v14-AC_EStd | EPr | CZ11 | 14 | AC_EStd | 21.9794 | 352429.8438 | 133157.6562 | 0 | 99493.7734 | 0 | 57389.8789 | 0 | 0 | 62388.8594 | 0 | 0 | 0 | 0 | 10203.4938 | 110.3944 | 7960.4531 | 2132.6483 | 1725.5283 | 193413% | -309884% | 3.821% | 0% | 100% | 0% | 1725.5283 | 119778.7383 | 929.483
EPr-w11-v14-AC_EHi | EPr | CZ11 | 14 | AC_EHi | 19.2103 | 342450.375 | 133157.6562 | 0 | 99493.7734 | 0 | 47410.4062 | 0 | 0 | 62388.8594 | 0 | 0 | 0 | 0 | 10203.4938 | 110.3944 | 7960.4531 | 2132.6483 | 1648.0876 | 193413% | -309884% | 3.821% | 0% | 100% | 0% | 1648.0876 | 109799.2656 | 852.0423
EPr-w11-v14-PVAV_Std | EPr | CZ11 | 14 | PVAV_Std | 38.3637 | 352964.2188 | 133157.6562 | 0 | 99493.7734 | 220.7672 | 69011.6016 | 0 | 467.2174 | 50613.1914 | 0 | 0 | 0 | 0 | 10471.1642 | 110.3944 | 8227.1232 | 2133.6462 | 1756.3395 | 220182% | -141570% | 0% | 0% | 0% | 0% | 1756.3395 | 120312.7776 | 933.6272
EPr-w11-v14-PVAV_Hi | EPr | CZ11 | 14 | PVAV_Hi | 30.1463 | 335677.1562 | 133157.6562 | 0 | 99493.7734 | 427.7676 | 53122.7617 | 0 | 499.7522 | 48975.3477 | 0 | 0 | 0 | 0 | 9949.513 | 110.3944 | 7705.3958 | 2133.7214 | 1570.0185 | 218732% | -136515% | 0% | 0% | 0% | 0% | 1570.0185 | 103025.6292 | 799.4789
EPr-w11-v14-VRF_HP_OAU0 | EPr | CZ11 | 14 | VRF_HP_OAU0 | 15.9982 | 388574.7188 | 133157.6562 | 0 | 99493.7734 | 47821.6328 | 56407.957 | 0 | 0 | 51693.9297 | 0 | 0 | 0 | 0 | 2242.6144 | 110.3944 | 0 | 2132.22 | 1209.9665 | 145230% | -151579% | 0% | 0% | 0% | 0% | 1209.9665 | 155923.5195 | 1209.9665
EPr-w11-v14-VRF_HP_OAU1 | EPr | CZ11 | 14 | VRF_HP_OAU1 | 14.3217 | 377554.4688 | 133157.6562 | 0 | 99493.7734 | 43427.2852 | 49781.8594 | 0 | 0 | 51693.9297 | 0 | 0 | 0 | 0 | 2242.6144 | 110.3944 | 0 | 2132.22 | 1124.4479 | 145230% | -151579% | 0% | 0% | 0% | 0% | 1124.4479 | 144903.0742 | 1124.4479
EPr-w11-v14-VRF_HP_OAU2 | EPr | CZ11 | 14 | VRF_HP_OAU2 | 12.8646 | 367959.0938 | 133157.6562 | 0 | 99493.7734 | 39450.5977 | 44163.3164 | 0 | 0 | 51693.9297 | 0 | 0 | 0 | 0 | 2242.6144 | 110.3944 | 0 | 2132.22 | 1049.9889 | 145230% | -151579% | 0% | 0% | 0% | 0% | 1049.9889 | 135307.8438 | 1049.9889
EPr-w11-v14-VRF_HR_OAU0 | EPr | CZ11 | 14 | VRF_HR_OAU0 | 17.1767 | 377282.875 | 133157.6562 | 0 | 99493.7734 | 41209.7812 | 51823.6055 | 0 | 0 | 51598.1367 | 0 | 0 | 0 | 0 | 2242.6059 | 110.3944 | 0 | 2132.2114 | 1122.3406 | 144337% | -150609% | 0% | 0% | 0% | 0% | 1122.3406 | 144631.5234 | 1122.3406
EPr-w11-v14-VRF_HR_OAU1 | EPr | CZ11 | 14 | VRF_HR_OAU1 | 15.4466 | 367227.0938 | 133157.6562 | 0 | 99493.7734 | 37245.3008 | 45732.4219 | 0 | 0 | 51598.1367 | 0 | 0 | 0 | 0 | 2242.6059 | 110.3944 | 0 | 2132.2114 | 1044.3087 | 144337% | -150609% | 0% | 0% | 0% | 0% | 1044.3087 | 134575.8594 | 1044.3087
EPr-w11-v14-VRF_HR_OAU2 | EPr | CZ11 | 14 | VRF_HR_OAU2 | 13.9421 | 358599.6875 | 133157.6562 | 0 | 99493.7734 | 33709.0469 | 40641.2305 | 0 | 0 | 51598.1367 | 0 | 0 | 0 | 0 | 2242.6059 | 110.3944 | 0 | 2132.2114 | 977.3597 | 144337% | -150609% | 0% | 0% | 0% | 0% | 977.3597 | 125948.4141 | 977.3597
Htl-w11-v14-FPFC_1 | Htl | CZ11 | 14 | FPFC_1 | 732.6119 | 4055676.75 | 566447.625 | 0 | 1692748 | 9483.3066 | 820817.4375 | 16105.1523 | 349229.75 | 600844.5 | 0 | 0 | 0 | 0 | 158290.391 | 0 | 121642.2298 | 36648.151 | 25979.9329 | 952622% | -1800860% | 92.46% | 0% | 8100% | 0% | 25979.9329 | 1780374.9941 | 13815.71
Htl-w11-v14-FPFC_2 | Htl | CZ11 | 14 | FPFC_2 | 671.3467 | 3861678.5 | 566447.625 | 0 | 1692748 | 22202.8984 | 591715.5 | 36975.875 | 349297.1562 | 602290.3125 | 0 | 0 | 0 | 0 | 135883.9091 | 0 | 99235.7581 | 36648.1664 | 22071.9013 | 952622% | -1800860% | 92.46% | 0% | 8100% | 0% | 22071.9013 | 1565505.8672 | 12148.3255
Htl-w11-v14-VRF_HP_OAU0 | Htl | CZ11 | 14 | VRF_HP_OAU0 | 1004.489 | 4369382 | 566447.625 | 0 | 1692748 | 796522.5625 | 847455.125 | 0 | 1121.6216 | 465085.9688 | 0 | 0 | 0 | 0 | 36647.8566 | 0 | 0 | 36647.8566 | 16375.0378 | 871978% | -905675% | 5.707% | 0% | 500% | 0% | 16375.0378 | 2110185.2778 | 16375.0378
Htl-w11-v14-VRF_HP_OAU1 | Htl | CZ11 | 14 | VRF_HP_OAU1 | 907.9666 | 4159700 | 566447.625 | 0 | 1692748 | 710524.6875 | 723771.375 | 0 | 1121.6216 | 465085.9688 | 0 | 0 | 0 | 0 | 36647.8566 | 0 | 0 | 36647.8566 | 14747.9083 | 871978% | -905675% | 5.707% | 0% | 500% | 0% | 14747.9083 | 1900503.6528 | 14747.9083
Htl-w11-v14-VRF_HP_OAU2 | Htl | CZ11 | 14 | VRF_HP_OAU2 | 835.7545 | 3997685 | 566447.625 | 0 | 1692748 | 640686.5625 | 631593.8125 | 0 | 1121.6216 | 465085.9688 | 0 | 0 | 0 | 0 | 36647.8566 | 0 | 0 | 36647.8566 | 13490.6666 | 871978% | -905675% | 5.707% | 0% | 500% | 0% | 13490.6666 | 1738487.9653 | 13490.6666
Htl-w11-v14-VRF_HR_OAU0 | Htl | CZ11 | 14 | VRF_HR_OAU0 | 981.4542 | 4257311 | 566447.625 | 0 | 1692748 | 723035.75 | 809650.375 | 0 | 1121.6216 | 464306.5 | 0 | 0 | 0 | 0 | 36647.7824 | 0 | 0 | 36647.7824 | 15505.3666 | 874849% | -908596% | 82.18% | 0% | 6600% | 600% | 15505.3666 | 1998114.2466 | 15505.3666
Htl-w11-v14-VRF_HR_OAU1 | Htl | CZ11 | 14 | VRF_HR_OAU1 | 889.4972 | 4056874.25 | 566447.625 | 0 | 1692748 | 641660.6875 | 690555.9375 | 0 | 1121.6216 | 464339.4688 | 0 | 0 | 0 | 0 | 36647.7824 | 0 | 0 | 36647.7824 | 13949.9791 | 875714% | -909501% | 81.04% | 0% | 6500% | 600% | 13949.9791 | 1797677.7153 | 13949.9791
Htl-w11-v14-VRF_HR_OAU2 | Htl | CZ11 | 14 | VRF_HR_OAU2 | 819.2943 | 3902098.75 | 566447.625 | 0 | 1692748 | 575606.5625 | 601834.1875 | 0 | 1121.6216 | 464339.4688 | 0 | 0 | 0 | 0 | 36647.7824 | 0 | 0 | 36647.7824 | 12748.9183 | 875714% | -909501% | 81.04% | 0% | 6500% | 600% | 12748.9183 | 1642901.8403 | 12748.9183
OfS-w12-v14-AC_S1Std | OfS | CZ12 | 14 | AC_S1Std | 42.0348 | 105020.3438 | 31593.9805 | 0 | 50648.0078 | 0 | 12422.9922 | 0 | 0 | 10355.5176 | 0 | 0 | 0 | 0 | 417.5785 | 0 | 239.8006 | 177.7778 | 200.7413 | 30791% | -43588% | 0% | 0% | 0% | 0% | 200.7413 | 22778.5098 | 176.7612
OfS-w12-v14-AC_S0Std | OfS | CZ12 | 14 | AC_S0Std | 42.0349 | 108719.0391 | 31593.9805 | 0 | 50648.0078 | 0 | 16121.4736 | 0 | 0 | 10355.7246 | 0 | 0 | 0 | 0 | 417.439 | 0 | 239.6621 | 177.777 | 229.4293 | 30791% | -43589% | 0% | 0% | 0% | 0% | 229.4293 | 26477.1982 | 205.4631
OfS-w12-v14-AC_SHi | OfS | CZ12 | 14 | AC_SHi | 36.9472 | 97285.6094 | 31593.9805 | 0 | 50648.0078 | 0 | 9719.0713 | 0 | 0 | 5324.6523 | 0 | 0 | 0 | 0 | 450.9512 | 0 | 273.1003 | 177.8509 | 144.0493 | 31180% | -34198% | 0% | 0% | 0% | 0% | 144.0493 | 15043.7236 | 116.7393
OfS-w12-v14-AC_EStd | OfS | CZ12 | 14 | AC_EStd | 43.3264 | 103503.375 | 31593.9805 | 0 | 50648.0078 | 0 | 13015.6162 | 0 | 0 | 8245.8809 | 0 | 0 | 0 | 0 | 428.96 | 0 | 251.1273 | 177.8327 | 190.1019 | 31142% | -33820% | 0% | 0% | 0% | 0% | 190.1019 | 21261.4971 | 164.9892
OfS-w12-v14-AC_EHi | OfS | CZ12 | 14 | AC_EHi | 39.8521 | 101240.0938 | 31593.9805 | 0 | 50648.0078 | 0 | 10752.3408 | 0 | 0 | 8245.8809 | 0 | 0 | 0 | 0 | 428.96 | 0 | 251.1273 | 177.8327 | 172.5389 | 31142% | -33820% | 0% | 0% | 0% | 0% | 172.5389 | 18998.2217 | 147.4262
OfS-w12-v14-PVAV_Std | OfS | CZ12 | 14 | PVAV_Std | 45.8279 | 104767.3281 | 31593.9805 | 0 | 50648.0078 | 22.9714 | 17267.0703 | 0 | 271.8539 | 4963.502 | 0 | 0 | 0 | 0 | 498.8512 | 0 | 321.0982 | 177.7531 | 206.9069 | 0% | 0% | 0% | 0% | 0% | 0% | 206.9069 | 22525.3975 | 174.7971
OfS-w12-v14-PVAV_Hi | OfS | CZ12 | 14 | PVAV_Hi | 40.1267 | 100638.9688 | 31593.9805 | 0 | 50648.0078 | 44.2072 | 13055.3838 | 0 | 273.0356 | 5024.4141 | 0 | 0 | 0 | 0 | 406.4752 | 0 | 228.7223 | 177.7527 | 165.6333 | 0% | 0% | 2.999% | 0% | 0% | 100% | 165.6333 | 18397.0407 | 142.761
OfS-w12-v14-VRF_HP_OAU0 | OfS | CZ12 | 14 | VRF_HP_OAU0 | 40.7297 | 104677.6797 | 31593.9805 | 0 | 50648.0078 | 2281.2522 | 15103.79 | 0 | 0 | 5050.7783 | 0 | 0 | 0 | 0 | 177.767 | 0 | 0 | 177.767 | 174.102 | 28712% | -30039% | 0% | 0% | 0% | 0% | 174.102 | 22435.8206 | 174.102
OfS-w12-v14-VRF_HP_OAU1 | OfS | CZ12 | 14 | VRF_HP_OAU1 | 38.4707 | 102660.3047 | 31593.9805 | 0 | 50648.0078 | 2061.9475 | 13305.7305 | 0 | 0 | 5050.7783 | 0 | 0 | 0 | 0 | 177.767 | 0 | 0 | 177.767 | 158.4472 | 28712% | -30039% | 0% | 0% | 0% | 0% | 158.4472 | 20418.4563 | 158.4472
OfS-w12-v14-VRF_HP_OAU2 | OfS | CZ12 | 14 | VRF_HP_OAU2 | 36.576 | 100969.1797 | 31593.9805 | 0 | 50648.0078 | 1866.9873 | 11809.5342 | 0 | 0 | 5050.7783 | 0 | 0 | 0 | 0 | 177.767 | 0 | 0 | 177.767 | 145.3238 | 28712% | -30039% | 0% | 0% | 0% | 0% | 145.3238 | 18727.2998 | 145.3238
OfS-w12-v14-VRF_HR_OAU0 | OfS | CZ12 | 14 | VRF_HR_OAU0 | 39.8811 | 103269.1875 | 31593.9805 | 0 | 50648.0078 | 1911.3533 | 14057.8838 | 0 | 0 | 5058.0713 | 0 | 0 | 0 | 0 | 177.7505 | 0 | 0 | 177.7505 | 163.1719 | 28726% | -30047% | 0% | 0% | 0% | 0% | 163.1719 | 21027.3083 | 163.1719
OfS-w12-v14-VRF_HR_OAU1 | OfS | CZ12 | 14 | VRF_HR_OAU1 | 37.7276 | 101410.6016 | 31593.9805 | 0 | 50648.0078 | 1719.5836 | 12391.0742 | 0 | 0 | 5058.0713 | 0 | 0 | 0 | 0 | 177.7505 | 0 | 0 | 177.7505 | 148.7493 | 28726% | -30047% | 0% | 0% | 0% | 0% | 148.7493 | 19168.7291 | 148.7493
OfS-w12-v14-VRF_HR_OAU2 | OfS | CZ12 | 14 | VRF_HR_OAU2 | 35.9206 | 99837.25 | 31593.9805 | 0 | 50648.0078 | 1554.5768 | 10982.7188 | 0 | 0 | 5058.0713 | 0 | 0 | 0 | 0 | 177.7505 | 0 | 0 | 177.7505 | 136.54 | 28726% | -30047% | 0% | 0% | 0% | 0% | 136.54 | 17595.3668 | 136.54
OfL-w12-v14-FPFC_1 | OfL | CZ12 | 14 | FPFC_1 | 527.6898 | 1824632.375 | 500422.4062 | 0 | 883691.5 | 335.5852 | 268106.3125 | 4472.9287 | 92632.2188 | 74972.5781 | 0 | 0 | 0 | 0 | 7293.1238 | 0 | 4329.0272 | 2964.096 | 3816.6251 | 411461% | -791737% | 0% | 0% | 0% | 0% | 3816.6251 | 436046.6946 | 3383.7224
OfL-w12-v14-FPFC_2 | OfL | CZ12 | 14 | FPFC_2 | 498.3108 | 1757293 | 500422.4062 | 0 | 883691.5 | 736.1614 | 193229.6875 | 12018.8438 | 92258.6797 | 74936.9688 | 0 | 0 | 0 | 0 | 5521.1091 | 0 | 2556.9696 | 2964.1386 | 3058.3102 | 411461% | -791737% | 0% | 0% | 0% | 0% | 3058.3102 | 361161.4973 | 2802.6132
OfL-w12-v14-VRF_HP_OAU0 | OfL | CZ12 | 14 | VRF_HP_OAU0 | 662.7319 | 1770493.125 | 500422.4062 | 0 | 883691.5 | 13773.3633 | 282457.25 | 0 | 213.4769 | 89936.3672 | 0 | 0 | 0 | 0 | 2963.6566 | 0 | 0 | 2963.6566 | 2998.3123 | 488700% | -511231% | 0% | 0% | 0% | 0% | 2998.3123 | 386380.4573 | 2998.3123
OfL-w12-v14-VRF_HP_OAU1 | OfL | CZ12 | 14 | VRF_HP_OAU1 | 604.6044 | 1718477.75 | 500422.4062 | 0 | 883691.5 | 11815.459 | 232400.0469 | 0 | 213.4769 | 89936.3672 | 0 | 0 | 0 | 0 | 2963.6566 | 0 | 0 | 2963.6566 | 2594.6751 | 488700% | -511231% | 0% | 0% | 0% | 0% | 2594.6751 | 334365.3499 | 2594.6751
OfL-w12-v14-VRF_HP_OAU2 | OfL | CZ12 | 14 | VRF_HP_OAU2 | 572.6025 | 1689773.5 | 500422.4062 | 0 | 883691.5 | 10721.873 | 204789.2188 | 0 | 213.4769 | 89936.3672 | 0 | 0 | 0 | 0 | 2963.6566 | 0 | 0 | 2963.6566 | 2371.9289 | 488700% | -511231% | 0% | 0% | 0% | 0% | 2371.9289 | 305660.9359 | 2371.9289
OfL-w12-v14-VRF_HR_OAU0 | OfL | CZ12 | 14 | VRF_HR_OAU0 | 641.9423 | 1749842.75 | 500422.4062 | 0 | 883691.5 | 11616.3721 | 262150.0625 | 0 | 213.4769 | 91750.5 | 0 | 0 | 0 | 0 | 2963.6378 | 0 | 0 | 2963.6378 | 2838.068 | 504777% | -528082% | 0% | 0% | 0% | 0% | 2838.068 | 365730.4114 | 2838.068
OfL-w12-v14-VRF_HR_OAU1 | OfL | CZ12 | 14 | VRF_HR_OAU1 | 587.7536 | 1701565.75 | 500422.4062 | 0 | 883691.5 | 9919.4551 | 215570.0156 | 0 | 213.4769 | 91750.5 | 0 | 0 | 0 | 0 | 2963.6378 | 0 | 0 | 2963.6378 | 2463.4388 | 504777% | -528082% | 0% | 0% | 0% | 0% | 2463.4388 | 317453.4476 | 2463.4388
OfL-w12-v14-VRF_HR_OAU2 | OfL | CZ12 | 14 | VRF_HR_OAU2 | 557.9487 | 1675156.625 | 500422.4062 | 0 | 883691.5 | 8931.0371 | 190149.5938 | 0 | 213.4769 | 91750.5 | 0 | 0 | 0 | 0 | 2963.6378 | 0 | 0 | 2963.6378 | 2258.5062 | 504777% | -528082% | 0% | 0% | 0% | 0% | 2258.5062 | 291044.6077 | 2258.5062
EPr-w12-v14-AC_S1Std | EPr | CZ12 | 14 | AC_S1Std | 5.7744 | 332329.0938 | 133157.6562 | 0 | 99493.7734 | 0 | 41307.8359 | 0 | 0 | 58369.9062 | 0 | 0 | 0 | 0 | 10297.4816 | 110.3944 | 7997.3024 | 2189.7846 | 1573.2295 | 1702.9553 | -3539.1809 | 0 | 0 | 0 | 0 | 1573.2295 | 99677.7422 | 773.4993
EPr-w12-v14-AC_S0Std | EPr | CZ12 | 14 | AC_S0Std | 5.7744 | 337428.875 | 133157.6562 | 0 | 99493.7734 | 0 | 46407.3359 | 0 | 0 | 58370.0312 | 0 | 0 | 0 | 0 | 10297.2179 | 110.3944 | 7997.0394 | 2189.7842 | 1612.7763 | 1702.9663 | -3539.2021 | 0 | 0 | 0 | 0 | 1612.7763 | 104777.3672 | 813.0724
EPr-w12-v14-AC_SHi | EPr | CZ12 | 14 | AC_SHi | 5.0026 | 307145.3125 | 133157.6562 | 0 | 99493.7734 | 0 | 32589.1855 | 0 | 0 | 41904.6875 | 0 | 0 | 0 | 0 | 10417.0797 | 110.3944 | 8116.7366 | 2189.9454 | 1389.7461 | 1673.4055 | -2921.9338 | 0 | 0 | 0 | 0 | 1389.7461 | 74493.873 | 578.0725
EPr-w12-v14-AC_EStd | EPr | CZ12 | 14 | AC_EStd | 7.7039 | 334985.1562 | 133157.6562 | 0 | 99493.7734 | 0 | 44730.3789 | 0 | 0 | 57603.4453 | 0 | 0 | 0 | 0 | 10130.5875 | 110.3944 | 7830.2746 | 2189.9194 | 1577.1379 | 1726.7251 | -2994.4646 | 0 | 0 | 0 | 0 | 1577.1379 | 102333.8242 | 794.1105
EPr-w12-v14-AC_EHi | EPr | CZ12 | 14 | AC_EHi | 6.897 | 327207.0312 | 133157.6562 | 0 | 99493.7734 | 0 | 36952.25 | 0 | 0 | 57603.4453 | 0 | 0 | 0 | 0 | 10130.5875 | 110.3944 | 7830.2746 | 2189.9194 | 1516.7797 | 1726.7251 | -2994.4646 | 0 | 0 | 0 | 0 | 1516.7797 | 94555.6953 | 733.7522
EPr-w12-v14-PVAV_Std | EPr | CZ12 | 14 | PVAV_Std | 17.5837 | 332526.6562 | 133157.6562 | 0 | 99493.7734 | 216.7339 | 52763.5039 | 0 | 474.7405 | 46420.1367 | 0 | 0 | 0 | 0 | 10423.4419 | 110.3944 | 8122.2406 | 2190.8094 | 1587.255 | 1780.2007 | -1347.5128 | 0 | 0 | 0 | 0 | 1587.255 | 99875.1151 | 775.0309
EPr-w12-v14-PVAV_Hi | EPr | CZ12 | 14 | PVAV_Hi | 14.3388 | 319093.9688 | 133157.6562 | 0 | 99493.7734 | 422.4626 | 40682.2891 | 0 | 477.5936 | 44860.1875 | 0 | 0 | 0 | 0 | 9901.0944 | 110.3944 | 7599.8131 | 2190.8883 | 1430.7754 | 1766.3574 | -1304.8783 | 0 | 0 | 0 | 0 | 1430.7754 | 86442.5328 | 670.7941
EPr-w12-v14-VRF_HP_OAU0 | EPr | CZ12 | 14 | VRF_HP_OAU0 | 6.0218 | 374748.1562 | 133157.6562 | 0 | 99493.7734 | 46183.6562 | 44572.6367 | 0 | 0 | 51340.4453 | 0 | 0 | 0 | 0 | 2299.8864 | 110.3944 | 0 | 2189.4917 | 1102.6707 | 1431.6334 | -1497.323 | 0 | 0 | 0 | 0 | 1102.6707 | 142096.7383 | 1102.6707
EPr-w12-v14-VRF_HP_OAU1 | EPr | CZ12 | 14 | VRF_HP_OAU1 | 5.5019 | 365158 | 133157.6562 | 0 | 99493.7734 | 41822.6055 | 39343.4883 | 0 | 0 | 51340.4453 | 0 | 0 | 0 | 0 | 2299.8864 | 110.3944 | 0 | 2189.4917 | 1028.2507 | 1431.6334 | -1497.323 | 0 | 0 | 0 | 0 | 1028.2507 | 132506.5391 | 1028.2507
EPr-w12-v14-VRF_HP_OAU2 | EPr | CZ12 | 14 | VRF_HP_OAU2 | 5.081 | 356953.8125 | 133157.6562 | 0 | 99493.7734 | 37982.543 | 34979.4375 | 0 | 0 | 51340.4453 | 0 | 0 | 0 | 0 | 2299.8864 | 110.3944 | 0 | 2189.4917 | 964.5868 | 1431.6334 | -1497.323 | 0 | 0 | 0 | 0 | 964.5868 | 124302.4258 | 964.5868
EPr-w12-v14-VRF_HR_OAU0 | EPr | CZ12 | 14 | VRF_HR_OAU0 | 6.598 | 363983.9375 | 133157.6562 | 0 | 99493.7734 | 39821.8945 | 40242.5742 | 0 | 0 | 51268.2188 | 0 | 0 | 0 | 0 | 2299.8779 | 110.3944 | 0 | 2189.4838 | 1019.1417 | 1420.8591 | -1485.3528 | 0 | 0 | 0 | 0 | 1019.1417 | 131332.6875 | 1019.1417
EPr-w12-v14-VRF_HR_OAU1 | EPr | CZ12 | 14 | VRF_HR_OAU1 | 6.0129 | 355474.875 | 133157.6562 | 0 | 99493.7734 | 35953.3555 | 35602.0156 | 0 | 0 | 51268.2188 | 0 | 0 | 0 | 0 | 2299.8779 | 110.3944 | 0 | 2189.4838 | 953.1111 | 1420.8591 | -1485.3528 | 0 | 0 | 0 | 0 | 953.1111 | 122823.5898 | 953.1111
EPr-w12-v14-VRF_HR_OAU2 | EPr | CZ12 | 14 | VRF_HR_OAU2 | 5.5356 | 348131.3125 | 133157.6562 | 0 | 99493.7734 | 32554.0176 | 31657.8301 | 0 | 0 | 51268.2188 | 0 | 0 | 0 | 0 | 2299.8779 | 110.3944 | 0 | 2189.4838 | 896.1253 | 1420.8591 | -1485.3528 | 0 | 0 | 0 | 0 | 896.1253 | 115480.0664 | 896.1253
Htl-w12-v14-FPFC_1 | Htl | CZ12 | 14 | FPFC_1 | 721.208 | 3976225 | 566447.625 | 0 | 1692748 | 9888.5928 | 725293.4375 | 10499.1748 | 336759.8125 | 634587.625 | 0 | 0 | 0 | 0 | 164604.9587 | 0 | 126356.2138 | 38248.745 | 25878.29 | 9795.1104 | -18880.7227 | 0.068485 | 0 | 6 | 0 | 25878.29 | 1706529.4678 | 13242.6687
Htl-w12-v14-FPFC_2 | Htl | CZ12 | 14 | FPFC_2 | 667.4831 | 3796598.25 | 566447.625 | 0 | 1692748 | 25618.832 | 507992.4688 | 31296.1016 | 336769.2812 | 635724.5 | 0 | 0 | 0 | 0 | 139254.528 | 0 | 101005.7318 | 38248.7578 | 21787.9486 | 9795.1104 | -18880.7227 | 0.068485 | 0 | 6 | 0 | 21787.9486 | 1506105.082 | 11687.3754
Htl-w12-v14-VRF_HP_OAU0 | Htl | CZ12 | 14 | VRF_HP_OAU0 | 907.0268 | 4132330.5 | 566447.625 | 0 | 1692748 | 783935.8125 | 622924.9375 | 0 | 1121.6216 | 465152.25 | 0 | 0 | 0 | 0 | 38248.8422 | 0 | 0 | 38248.8422 | 14535.5247 | 8281.2705 | -8613.1436 | 0.022828 | 0 | 2 | 0 | 14535.5247 | 1873134.6216 | 14535.5247
Htl-w12-v14-VRF_HP_OAU1 | Htl | CZ12 | 14 | VRF_HP_OAU1 | 826.3005 | 3957195 | 566447.625 | 0 | 1692748 | 700383 | 531342.5625 | 0 | 1121.6216 | 465152.25 | 0 | 0 | 0 | 0 | 38248.8422 | 0 | 0 | 38248.8422 | 13176.4756 | 8281.2705 | -8613.1436 | 0.022828 | 0 | 2 | 0 | 13176.4756 | 1697999.4341 | 13176.4756
Htl-w12-v14-VRF_HP_OAU2 | Htl | CZ12 | 14 | VRF_HP_OAU2 | 764.7094 | 3819950.25 | 566447.625 | 0 | 1692748 | 630959.25 | 463521.4062 | 0 | 1121.6216 | 465152.2812 | 0 | 0 | 0 | 0 | 38248.8422 | 0 | 0 | 38248.8422 | 12111.4554 | 8281.2734 | -8613.1455 | 0.022828 | 0 | 2 | 0 | 12111.4554 | 1560754.5591 | 12111.4554
Htl-w12-v14-VRF_HR_OAU0 | Htl | CZ12 | 14 | VRF_HR_OAU0 | 873.8115 | 4022644.25 | 566447.625 | 0 | 1692748 | 707025 | 593021.125 | 0 | 1121.6216 | 462280.6875 | 0 | 0 | 0 | 0 | 38248.791 | 0 | 0 | 38248.791 | 13684.3598 | 8239.7227 | -8567.1143 | 1.1072 | 0 | 95 | 2 | 13684.3598 | 1763448.4341 | 13684.3598
Htl-w12-v14-VRF_HR_OAU1 | Htl | CZ12 | 14 | VRF_HR_OAU1 | 798.3113 | 3856527.5 | 566447.625 | 0 | 1692748 | 628776.75 | 505181.125 | 0 | 1121.6216 | 462252.0625 | 0 | 0 | 0 | 0 | 38248.791 | 0 | 0 | 38248.791 | 12395.2929 | 8243.1709 | -8570.749 | 1.0958 | 0 | 94 | 2 | 12395.2929 | 1597331.5591 | 12395.2929
Htl-w12-v14-VRF_HR_OAU2 | Htl | CZ12 | 14 | VRF_HR_OAU2 | 741.4512 | 3726462 | 566447.625 | 0 | 1692748 | 563883.875 | 440007.7812 | 0 | 1121.6216 | 462252.0625 | 0 | 0 | 0 | 0 | 38248.791 | 0 | 0 | 38248.791 | 11385.979 | 8243.1709 | -8570.749 | 1.0958 | 0 | 94 | 2 | 11385.979 | 1467265.3403 | 11385.979
OfS-w13-v14-AC_S1Std | OfS | CZ13 | 14 | AC_S1Std | 42.6842 | 109891.6641 | 31593.9805 | 0 | 50648.0078 | 0 | 17196.6016 | 0 | 0 | 10453.166 | 0 | 0 | 0 | 0 | 403.5156 | 0 | 232.5685 | 170.9471 | 237.819 | 305.5176 | -408.0205 | 0 | 0 | 0 | 0 | 237.819 | 27649.7676 | 214.5622
OfS-w13-v14-AC_S0Std | OfS | CZ13 | 14 | AC_S0Std | 42.6845 | 113101.5234 | 31593.9805 | 0 | 50648.0078 | 0 | 20406.9121 | 0 | 0 | 10452.7471 | 0 | 0 | 0 | 0 | 403.4066 | 0 | 232.4603 | 170.9463 | 262.717 | 305.5255 | -408.007 | 0 | 0 | 0 | 0 | 262.717 | 30859.6592 | 239.471
OfS-w13-v14-AC_SHi | OfS | CZ13 | 14 | AC_SHi | 37.8261 | 101299.7188 | 31593.9805 | 0 | 50648.0078 | 0 | 13617.0439 | 0 | 0 | 5440.7695 | 0 | 0 | 0 | 0 | 438.9493 | 0 | 267.9292 | 171.0201 | 174.6815 | 309.8714 | -359.809 | 0 | 0 | 0 | 0 | 174.6815 | 19057.8135 | 147.8886
OfS-w13-v14-AC_EStd | OfS | CZ13 | 14 | AC_EStd | 44.3831 | 109142.5078 | 31593.9805 | 0 | 50648.0078 | 0 | 18228.8242 | 0 | 0 | 8671.8047 | 0 | 0 | 0 | 0 | 418.4653 | 0 | 247.4643 | 171.0009 | 233.4953 | 310.272 | -355.6559 | 0 | 0 | 0 | 0 | 233.4953 | 26900.6289 | 208.7489
OfS-w13-v14-AC_EHi | OfS | CZ13 | 14 | AC_EHi | 40.7712 | 105972.7031 | 31593.9805 | 0 | 50648.0078 | 0 | 15059.0225 | 0 | 0 | 8671.8047 | 0 | 0 | 0 | 0 | 418.4653 | 0 | 247.4643 | 171.0009 | 208.8977 | 310.272 | -355.6559 | 0 | 0 | 0 | 0 | 208.8977 | 23730.8271 | 184.1512
OfS-w13-v14-PVAV_Std | OfS | CZ13 | 14 | PVAV_Std | 46.953 | 110938.7812 | 31593.9805 | 0 | 50648.0078 | 20.6342 | 22754.7344 | 0 | 256.5853 | 5664.8931 | 0 | 0 | 0 | 0 | 462.6651 | 0 | 291.6362 | 171.0291 | 251.8511 | 0 | 0 | 0 | 0 | 0 | 0 | 251.8511 | 28696.8469 | 222.6875
OfS-w13-v14-PVAV_Hi | OfS | CZ13 | 14 | PVAV_Hi | 41.015 | 105446.1562 | 31593.9805 | 0 | 50648.0078 | 38.4962 | 17210.9824 | 0 | 258.1268 | 5696.6006 | 0 | 0 | 0 | 0 | 382.7603 | 0 | 211.7295 | 171.0308 | 201.2376 | 0 | 0 | 0 | 0 | 0 | 0 | 201.2376 | 23204.2061 | 180.0646
OfS-w13-v14-VRF_HP_OAU0 | OfS | CZ13 | 14 | VRF_HP_OAU0 | 42.278 | 109466.25 | 31593.9805 | 0 | 50648.0078 | 2166.5989 | 19733.7637 | 0 | 0 | 5324.0039 | 0 | 0 | 0 | 0 | 170.9197 | 0 | 0 | 170.9197 | 211.2611 | 309.0247 | -323.0406 | 0 | 0 | 0 | 0 | 211.2611 | 27224.3665 | 211.2611
OfS-w13-v14-VRF_HP_OAU1 | OfS | CZ13 | 14 | VRF_HP_OAU1 | 39.8396 | 106920.3125 | 31593.9805 | 0 | 50648.0078 | 1958.4716 | 17395.9453 | 0 | 0 | 5324.0039 | 0 | 0 | 0 | 0 | 170.9197 | 0 | 0 | 170.9197 | 191.5045 | 309.0247 | -323.0406 | 0 | 0 | 0 | 0 | 191.5045 | 24678.4208 | 191.5045
OfS-w13-v14-VRF_HP_OAU2 | OfS | CZ13 | 14 | VRF_HP_OAU2 | 37.796 | 104766.5781 | 31593.9805 | 0 | 50648.0078 | 1774.7449 | 15425.9277 | 0 | 0 | 5324.0039 | 0 | 0 | 0 | 0 | 170.9197 | 0 | 0 | 170.9197 | 174.7915 | 309.0247 | -323.0406 | 0 | 0 | 0 | 0 | 174.7915 | 22524.6765 | 174.7915
OfS-w13-v14-VRF_HR_OAU0 | OfS | CZ13 | 14 | VRF_HR_OAU0 | 41.4402 | 107779.6406 | 31593.9805 | 0 | 50648.0078 | 1829.2644 | 18383.416 | 0 | 0 | 5325.0747 | 0 | 0 | 0 | 0 | 170.9019 | 0 | 0 | 170.9019 | 198.173 | 308.1987 | -322.1943 | 0 | 0 | 0 | 0 | 198.173 | 25537.7551 | 198.173
OfS-w13-v14-VRF_HR_OAU1 | OfS | CZ13 | 14 | VRF_HR_OAU1 | 39.1081 | 105410.9844 | 31593.9805 | 0 | 50648.0078 | 1644.0686 | 16199.9424 | 0 | 0 | 5325.0747 | 0 | 0 | 0 | 0 | 170.9019 | 0 | 0 | 170.9019 | 179.7921 | 308.1987 | -322.1943 | 0 | 0 | 0 | 0 | 179.7921 | 23169.0857 | 179.7921
OfS-w13-v14-VRF_HR_OAU2 | OfS | CZ13 | 14 | VRF_HR_OAU2 | 37.1518 | 103411.8516 | 31593.9805 | 0 | 50648.0078 | 1484.2234 | 14360.6445 | 0 | 0 | 5325.0747 | 0 | 0 | 0 | 0 | 170.9019 | 0 | 0 | 170.9019 | 164.2788 | 308.1987 | -322.1943 | 0 | 0 | 0 | 0 | 164.2788 | 21169.9426 | 164.2788
OfL-w13-v14-FPFC_1 | OfL | CZ13 | 14 | FPFC_1 | 533.2781 | 1846115 | 500422.4062 | 0 | 883691.5 | 283.3069 | 285963.75 | 5661.937 | 93040.5391 | 77052.3984 | 0 | 0 | 0 | 0 | 6496.7085 | 0 | 3658.5581 | 2838.151 | 3907.0542 | 4035.9333 | -7631.7021 | 0 | 0 | 0 | 0 | 3907.0542 | 456339.9944 | 3541.1984
OfL-w13-v14-FPFC_2 | OfL | CZ13 | 14 | FPFC_2 | 505.0688 | 1779468.875 | 500422.4062 | 0 | 883691.5 | 618.9249 | 211315.7812 | 13846.5527 | 92566.2578 | 77008.8984 | 0 | 0 | 0 | 0 | 5082.0854 | 0 | 2243.8979 | 2838.1872 | 3184.9063 | 4035.9333 | -7631.7021 | 0 | 0 | 0 | 0 | 3184.9063 | 381509.8624 | 2960.5165
OfL-w13-v14-VRF_HP_OAU0 | OfL | CZ13 | 14 | VRF_HP_OAU0 | 678.7822 | 1835242.375 | 500422.4062 | 0 | 883691.5 | 13710.4199 | 347289.5625 | 0 | 213.4769 | 89915.5469 | 0 | 0 | 0 | 0 | 2837.6886 | 0 | 0 | 2837.6886 | 3500.7611 | 4863.5815 | -5082.8467 | 0 | 0 | 0 | 0 | 3500.7611 | 451129.0062 | 3500.7611
OfL-w13-v14-VRF_HP_OAU1 | OfL | CZ13 | 14 | VRF_HP_OAU1 | 617.7266 | 1771809.5 | 500422.4062 | 0 | 883691.5 | 11787.1807 | 285780.5625 | 0 | 213.4769 | 89915.6172 | 0 | 0 | 0 | 0 | 2837.6886 | 0 | 0 | 2837.6886 | 3008.5275 | 4863.5815 | -5082.8467 | 0 | 0 | 0 | 0 | 3008.5275 | 387696.8372 | 3008.5275
OfL-w13-v14-VRF_HP_OAU2 | OfL | CZ13 | 14 | VRF_HP_OAU2 | 584.1791 | 1736744 | 500422.4062 | 0 | 883691.5 | 10650.9062 | 251851.375 | 0 | 213.4769 | 89915.6328 | 0 | 0 | 0 | 0 | 2837.6886 | 0 | 0 | 2837.6886 | 2736.4196 | 4863.5815 | -5082.8467 | 0 | 0 | 0 | 0 | 2736.4196 | 352631.3909 | 2736.4196
OfL-w13-v14-VRF_HR_OAU0 | OfL | CZ13 | 14 | VRF_HR_OAU0 | 658.8677 | 1812517 | 500422.4062 | 0 | 883691.5 | 11333.3232 | 322973.2812 | 0 | 213.4769 | 93884.1094 | 0 | 0 | 0 | 0 | 2837.6851 | 0 | 0 | 2837.6851 | 3324.4165 | 5214.4434 | -5449.4453 | 0 | 0 | 0 | 0 | 3324.4165 | 428404.1907 | 3324.4165
OfL-w13-v14-VRF_HR_OAU1 | OfL | CZ13 | 14 | VRF_HR_OAU1 | 601.6908 | 1753513.125 | 500422.4062 | 0 | 883691.5 | 9653.5703 | 265649.7188 | 0 | 213.4769 | 93884.1094 | 0 | 0 | 0 | 0 | 2837.6851 | 0 | 0 | 2837.6851 | 2866.5508 | 5214.4434 | -5449.4453 | 0 | 0 | 0 | 0 | 2866.5508 | 369400.8753 | 2866.5508
OfL-w13-v14-VRF_HR_OAU2 | OfL | CZ13 | 14 | VRF_HR_OAU2 | 570.2557 | 1721284.875 | 500422.4062 | 0 | 883691.5 | 8678.0459 | 234396.9219 | 0 | 213.4769 | 93884.1094 | 0 | 0 | 0 | 0 | 2837.6851 | 0 | 0 | 2837.6851 | 2616.459 | 5214.4434 | -5449.4453 | 0 | 0 | 0 | 0 | 2616.459 | 337172.554 | 2616.459
EPr-w13-v14-AC_S1Std | EPr | CZ13 | 14 | AC_S1Std | 14.6045 | 349502.1875 | 133157.6562 | 0 | 99493.7734 | 0 | 58208.0781 | 0 | 0 | 58642.8008 | 0 | 0 | 0 | 0 | 9547.1174 | 110.3944 | 7331.0035 | 2105.7186 | 1639.8632 | 1697.1985 | -3373.9502 | 0.15285 | 0 | 4 | 0 | 1639.8632 | 116850.8789 | 906.7628
EPr-w13-v14-AC_S0Std | EPr | CZ13 | 14 | AC_S0Std | 14.6044 | 354663.5 | 133157.6562 | 0 | 99493.7734 | 0 | 63369.1094 | 0 | 0 | 58643.4258 | 0 | 0 | 0 | 0 | 9546.9818 | 110.3944 | 7330.8685 | 2105.7181 | 1679.9041 | 1697.2021 | -3373.9568 | 0.15285 | 0 | 4 | 0 | 1679.9041 | 122012.5352 | 946.8173
EPr-w13-v14-AC_SHi | EPr | CZ13 | 14 | AC_SHi | 12.1975 | 321351.5 | 133157.6562 | 0 | 99493.7734 | 0 | 46329.125 | 0 | 0 | 42371.1484 | 0 | 0 | 0 | 0 | 9668.6035 | 110.3944 | 7452.3302 | 2105.8778 | 1433.5471 | 1677.5026 | -2836.0947 | 0.076423 | 0 | 2 | 0 | 1433.5471 | 88700.2734 | 688.3141
EPr-w13-v14-AC_EStd | EPr | CZ13 | 14 | AC_EStd | 19.2257 | 355574.3438 | 133157.6562 | 0 | 99493.7734 | 0 | 63795.332 | 0 | 0 | 59127.7109 | 0 | 0 | 0 | 0 | 9408.2522 | 110.3944 | 7192.007 | 2105.8498 | 1673.0835 | 1742.0264 | -2896.5784 | 0.26748 | 0 | 7 | 0 | 1673.0835 | 122923.043 | 953.8828
EPr-w13-v14-AC_EHi | EPr | CZ13 | 14 | AC_EHi | 16.8088 | 344481.0312 | 133157.6562 | 0 | 99493.7734 | 0 | 52702 | 0 | 0 | 59127.7109 | 0 | 0 | 0 | 0 | 9408.2522 | 110.3944 | 7192.007 | 2105.8498 | 1586.9993 | 1742.0264 | -2896.5784 | 0.26748 | 0 | 7 | 0 | 1586.9993 | 111829.7109 | 867.7986
EPr-w13-v14-PVAV_Std | EPr | CZ13 | 14 | PVAV_Std | 34.0875 | 354694.5312 | 133157.6562 | 0 | 99493.7734 | 193.2581 | 73751.3438 | 0 | 409.6879 | 47688.7773 | 0 | 0 | 0 | 0 | 9606.7469 | 110.3944 | 7389.5168 | 2106.8344 | 1686.0059 | 1771.3771 | -1256.1187 | 0.15285 | 0 | 4 | 0 | 1686.0059 | 122043.067 | 947.0542
EPr-w13-v14-PVAV_Hi | EPr | CZ13 | 14 | PVAV_Hi | 28.0926 | 336529.1875 | 133157.6562 | 0 | 99493.7734 | 365.6512 | 56786.3086 | 0 | 424.5768 | 46301.1914 | 0 | 0 | 0 | 0 | 9124.3328 | 110.3944 | 6907.0464 | 2106.8936 | 1496.7958 | 1756.3534 | -1222.292 | 0 | 0 | 0 | 0 | 1496.7958 | 103877.7281 | 806.0912
EPr-w13-v14-VRF_HP_OAU0 | EPr | CZ13 | 14 | VRF_HP_OAU0 | 15.3945 | 390094.9375 | 133157.6562 | 0 | 99493.7734 | 42415.0156 | 62915.4219 | 0 | 0 | 52113.3125 | 0 | 0 | 0 | 0 | 2215.7872 | 110.3944 | 0 | 2105.393 | 1221.7635 | 1505.2594 | -1572.3184 | 0 | 0 | 0 | 0 | 1221.7635 | 157443.75 | 1221.7635
EPr-w13-v14-VRF_HP_OAU1 | EPr | CZ13 | 14 | VRF_HP_OAU1 | 13.9327 | 378599 | 133157.6562 | 0 | 99493.7734 | 38378.2812 | 55456.2969 | 0 | 0 | 52113.207 | 0 | 0 | 0 | 0 | 2215.7872 | 110.3944 | 0 | 2105.393 | 1132.5548 | 1505.2594 | -1572.3184 | 0 | 0 | 0 | 0 | 1132.5548 | 145947.7852 | 1132.5548
EPr-w13-v14-VRF_HP_OAU2 | EPr | CZ13 | 14 | VRF_HP_OAU2 | 12.7246 | 368770 | 133157.6562 | 0 | 99493.7734 | 34815.6875 | 49189.8672 | 0 | 0 | 52113.1914 | 0 | 0 | 0 | 0 | 2215.7872 | 110.3944 | 0 | 2105.393 | 1056.2815 | 1505.2594 | -1572.3184 | 0 | 0 | 0 | 0 | 1056.2815 | 136118.7461 | 1056.2815
EPr-w13-v14-VRF_HR_OAU0 | EPr | CZ13 | 14 | VRF_HR_OAU0 | 16.9038 | 378728.875 | 133157.6562 | 0 | 99493.7734 | 36517.457 | 57576.6797 | 0 | 0 | 51983.4805 | 0 | 0 | 0 | 0 | 2215.7765 | 110.3944 | 0 | 2105.3819 | 1133.5623 | 1487.6208 | -1553.8656 | 0.076423 | 0 | 2 | 0 | 1133.5623 | 146077.6172 | 1133.5623
EPr-w13-v14-VRF_HR_OAU1 | EPr | CZ13 | 14 | VRF_HR_OAU1 | 15.2168 | 368326.9375 | 133157.6562 | 0 | 99493.7734 | 32969.6484 | 50722.5586 | 0 | 0 | 51983.4805 | 0 | 0 | 0 | 0 | 2215.7765 | 110.3944 | 0 | 2105.3819 | 1052.8433 | 1487.6208 | -1553.8656 | 0.076423 | 0 | 2 | 0 | 1052.8433 | 135675.6875 | 1052.8433
EPr-w13-v14-VRF_HR_OAU2 | EPr | CZ13 | 14 | VRF_HR_OAU2 | 13.7987 | 359527.75 | 133157.6562 | 0 | 99493.7734 | 29876.043 | 45017.0742 | 0 | 0 | 51983.4805 | 0 | 0 | 0 | 0 | 2215.7765 | 110.3944 | 0 | 2105.3819 | 984.5624 | 1487.6208 | -1553.8656 | 0.076423 | 0 | 2 | 0 | 984.5624 | 126876.5977 | 984.5624
Htl-w13-v14-FPFC_1 | Htl | CZ13 | 14 | FPFC_1 | 716.0414 | 4071144 | 566447.625 | 0 | 1692748 | 8627.1484 | 835297.6875 | 15367.6982 | 331602.75 | 621051.9375 | 0 | 0 | 0 | 0 | 146351.4317 | 0 | 110318.5715 | 36032.8934 | 24973.3143 | 9518.4854 | -17949.0391 | 0.54788 | 0 | 48 | 0 | 24973.3143 | 1796579.5234 | 13941.4571
Htl-w13-v14-FPFC_2 | Htl | CZ13 | 14 | FPFC_2 | 666.5999 | 3878770.75 | 566447.625 | 0 | 1692748 | 21040.2539 | 604889.5625 | 40383.5938 | 331101.125 | 622160.375 | 0 | 0 | 0 | 0 | 125158.0518 | 0 | 89125.161 | 36032.9088 | 21167.0407 | 9518.4854 | -17949.0391 | 0.54788 | 0 | 48 | 0 | 21167.0407 | 1579191.3164 | 12254.5246
Htl-w13-v14-VRF_HP_OAU0 | Htl | CZ13 | 14 | VRF_HP_OAU0 | 916.6836 | 4321205 | 566447.625 | 0 | 1692748 | 702105.6875 | 886185.5625 | 0 | 1121.6216 | 472595.375 | 0 | 0 | 0 | 0 | 36032.4378 | 0 | 0 | 36032.4378 | 16001.184 | 8257.7773 | -8580.9268 | 0.011414 | 0 | 1 | 0 | 16001.184 | 2062008.2466 | 16001.184
Htl-w13-v14-VRF_HP_OAU1 | Htl | CZ13 | 14 | VRF_HP_OAU1 | 833.8052 | 4115847.5 | 566447.625 | 0 | 1692748 | 626026.25 | 756907.6875 | 0 | 1121.6216 | 472595.2188 | 0 | 0 | 0 | 0 | 36032.4378 | 0 | 0 | 36032.4378 | 14407.61 | 8257.7773 | -8580.9268 | 0.011414 | 0 | 1 | 0 | 14407.61 | 1856650.7778 | 14407.61
Htl-w13-v14-VRF_HP_OAU2 | Htl | CZ13 | 14 | VRF_HP_OAU2 | 770.8766 | 3958058 | 566447.625 | 0 | 1692748 | 564551 | 660594.375 | 0 | 1121.6216 | 472595.2188 | 0 | 0 | 0 | 0 | 36032.4378 | 0 | 0 | 36032.4378 | 13183.1708 | 8257.7803 | -8580.9297 | 0.011414 | 0 | 1 | 0 | 13183.1708 | 1698862.2153 | 13183.1708
Htl-w13-v14-VRF_HR_OAU0 | Htl | CZ13 | 14 | VRF_HR_OAU0 | 890.2174 | 4206312 | 566447.625 | 0 | 1692748 | 633913.3125 | 842259.125 | 0 | 1121.6216 | 469821.5312 | 0 | 0 | 0 | 0 | 36032.3584 | 0 | 0 | 36032.3584 | 15109.617 | 8189.2529 | -8508.8408 | 0.6392 | 0 | 56 | 0 | 15109.617 | 1947115.5903 | 15109.617
Htl-w13-v14-VRF_HR_OAU1 | Htl | CZ13 | 14 | VRF_HR_OAU1 | 811.9958 | 4010617 | 566447.625 | 0 | 1692748 | 562222.875 | 718254.4375 | 0 | 1121.6216 | 469821.5312 | 0 | 0 | 0 | 0 | 36032.3584 | 0 | 0 | 36032.3584 | 13591.0228 | 8189.2529 | -8508.8408 | 0.6392 | 0 | 56 | 0 | 13591.0228 | 1751420.4653 | 13591.0228
Htl-w13-v14-VRF_HR_OAU2 | Htl | CZ13 | 14 | VRF_HR_OAU2 | 752.295 | 3861139.25 | 566447.625 | 0 | 1692748 | 504632.9375 | 626326.9375 | 0 | 1121.6216 | 469860.5312 | 0 | 0 | 0 | 0 | 36032.3584 | 0 | 0 | 36032.3584 | 12431.0701 | 8194.3174 | -8514.1445 | 0.6392 | 0 | 56 | 0 | 12431.0701 | 1601942.0278 | 12431.0701
OfS-w14-v14-AC_S1Std | OfS | CZ14 | 14 | AC_S1Std | 43.6725 | 110081.8047 | 31593.9805 | 0 | 50648.0078 | 0 | 17738.9316 | 0 | 0 | 10101.0195 | 0 | 0 | 0 | 0 | 424.1686 | 0 | 250.1853 | 173.9833 | 241.0566 | 298.834 | -435.4559 | 0.029994 | 0 | 1 | 0 | 241.0566 | 27839.9512 | 216.038
OfS-w14-v14-AC_S0Std | OfS | CZ14 | 14 | AC_S0Std | 43.6732 | 113138.4688 | 31593.9805 | 0 | 50648.0078 | 0 | 20795.5859 | 0 | 0 | 10101.0312 | 0 | 0 | 0 | 0 | 423.9645 | 0 | 249.9821 | 173.9823 | 264.756 | 298.8356 | -435.456 | 0.029994 | 0 | 1 | 0 | 264.756 | 30896.6172 | 239.7577
OfS-w14-v14-AC_SHi | OfS | CZ14 | 14 | AC_SHi | 39.0334 | 101384.3281 | 31593.9805 | 0 | 50648.0078 | 0 | 13913.7324 | 0 | 0 | 5228.6982 | 0 | 0 | 0 | 0 | 451.2874 | 0 | 277.2329 | 174.0545 | 176.2685 | 300.3928 | -354.5688 | 0.029994 | 0 | 1 | 0 | 176.2685 | 19142.4307 | 148.5453
OfS-w14-v14-AC_EStd | OfS | CZ14 | 14 | AC_EStd | 45.5089 | 109194.7422 | 31593.9805 | 0 | 50648.0078 | 0 | 18726.9434 | 0 | 0 | 8225.875 | 0 | 0 | 0 | 0 | 432.7075 | 0 | 258.6699 | 174.0378 | 235.0209 | 301.2695 | -350.7448 | 0.059988 | 0 | 2 | 0 | 235.0209 | 26952.8184 | 209.1539
OfS-w14-v14-AC_EHi | OfS | CZ14 | 14 | AC_EHi | 41.691 | 105938.3047 | 31593.9805 | 0 | 50648.0078 | 0 | 15470.5283 | 0 | 0 | 8225.875 | 0 | 0 | 0 | 0 | 432.7075 | 0 | 258.6699 | 174.0378 | 209.7511 | 301.2695 | -350.7448 | 0.059988 | 0 | 2 | 0 | 209.7511 | 23696.4033 | 183.8841
OfS-w14-v14-PVAV_Std | OfS | CZ14 | 14 | PVAV_Std | 47.7562 | 111291.1484 | 31593.9805 | 0 | 50648.0078 | 22.5733 | 23155.5684 | 0 | 302.6366 | 5568.4312 | 0 | 0 | 0 | 0 | 495.952 | 0 | 321.9241 | 174.0278 | 257.6143 | 0 | 0 | 0 | 0 | 0 | 0 | 257.6143 | 29049.2094 | 225.4219
OfS-w14-v14-PVAV_Hi | OfS | CZ14 | 14 | PVAV_Hi | 41.6811 | 105697.7266 | 31593.9805 | 0 | 50648.0078 | 42.0072 | 17520.1348 | 0 | 303.8545 | 5589.7764 | 0 | 0 | 0 | 0 | 399.4206 | 0 | 225.3898 | 174.0307 | 204.5558 | 0 | 0 | 0 | 0 | 0 | 0 | 204.5558 | 23455.7728 | 182.0168
OfS-w14-v14-VRF_HP_OAU0 | OfS | CZ14 | 14 | VRF_HP_OAU0 | 42.9855 | 109859.5859 | 31593.9805 | 0 | 50648.0078 | 2322.4399 | 20070.9219 | 0 | 0 | 5224.3604 | 0 | 0 | 0 | 0 | 173.9505 | 0 | 0 | 173.9505 | 214.3135 | 298.7489 | -309.1107 | 0 | 0 | 0 | 0 | 214.3135 | 27617.7222 | 214.3135
OfS-w14-v14-VRF_HP_OAU1 | OfS | CZ14 | 14 | VRF_HP_OAU1 | 40.3789 | 107254.9062 | 31593.9805 | 0 | 50648.0078 | 2109.9146 | 17678.7637 | 0 | 0 | 5224.3506 | 0 | 0 | 0 | 0 | 173.9505 | 0 | 0 | 173.9505 | 194.1011 | 298.7489 | -309.1107 | 0 | 0 | 0 | 0 | 194.1011 | 25013.0288 | 194.1011
OfS-w14-v14-VRF_HP_OAU2 | OfS | CZ14 | 14 | VRF_HP_OAU2 | 38.227 | 105067.1953 | 31593.9805 | 0 | 50648.0078 | 1923.6189 | 15677.3418 | 0 | 0 | 5224.3506 | 0 | 0 | 0 | 0 | 173.9505 | 0 | 0 | 173.9505 | 177.1244 | 298.7489 | -309.1107 | 0 | 0 | 0 | 0 | 177.1244 | 22825.3113 | 177.1244
OfS-w14-v14-VRF_HR_OAU0 | OfS | CZ14 | 14 | VRF_HR_OAU0 | 42.5486 | 108056.9141 | 31593.9805 | 0 | 50648.0078 | 1879.6298 | 18727.0059 | 0 | 0 | 5208.4209 | 0 | 0 | 0 | 0 | 173.9321 | 0 | 0 | 173.9321 | 200.3248 | 296.3867 | -306.7601 | 0 | 0 | 0 | 0 | 200.3248 | 25815.0565 | 200.3248
OfS-w14-v14-VRF_HR_OAU1 | OfS | CZ14 | 14 | VRF_HR_OAU1 | 40.0808 | 105644.8281 | 31593.9805 | 0 | 50648.0078 | 1694.9463 | 16499.584 | 0 | 0 | 5208.4209 | 0 | 0 | 0 | 0 | 173.9321 | 0 | 0 | 173.9321 | 181.6069 | 296.3867 | -306.7601 | 0 | 0 | 0 | 0 | 181.6069 | 23402.9512 | 181.6069
OfS-w14-v14-VRF_HR_OAU2 | OfS | CZ14 | 14 | VRF_HR_OAU2 | 37.8262 | 103595.7266 | 31593.9805 | 0 | 50648.0078 | 1535.4998 | 14610.0791 | 0 | 0 | 5208.271 | 0 | 0 | 0 | 0 | 173.9321 | 0 | 0 | 173.9321 | 165.7059 | 296.3867 | -306.7601 | 0 | 0 | 0 | 0 | 165.7059 | 21353.8499 | 165.7059
OfL-w14-v14-FPFC_1 | OfL | CZ14 | 14 | FPFC_1 | 522.6467 | 1853594.125 | 500422.4062 | 0 | 883691.5 | 358.814 | 292445.625 | 4745.7939 | 95052.9531 | 76878.2812 | 0 | 0 | 0 | 0 | 7575.8605 | 0 | 4681.5283 | 2894.3318 | 4074.5017 | 3754.8486 | -7699.8696 | 0 | 0 | 0 | 0 | 4074.5017 | 464735.6734 | 3606.3488
OfL-w14-v14-FPFC_2 | OfL | CZ14 | 14 | FPFC_2 | 491.177 | 1781529.625 | 500422.4062 | 0 | 883691.5 | 764.7991 | 213962.2812 | 11145.4111 | 94794.3281 | 76750.3984 | 0 | 0 | 0 | 0 | 5812.4173 | 0 | 2918.0371 | 2894.3814 | 3289.2729 | 3754.8486 | -7699.8696 | 0 | 0 | 0 | 0 | 3289.2729 | 386271.8069 | 2997.4692
OfL-w14-v14-VRF_HP_OAU0 | OfL | CZ14 | 14 | VRF_HP_OAU0 | 686.7355 | 1852394 | 500422.4062 | 0 | 883691.5 | 17951.4688 | 357067.1875 | 0 | 213.4769 | 93049.1406 | 0 | 0 | 0 | 0 | 2893.9674 | 0 | 0 | 2893.9674 | 3633.8627 | 5130.7285 | -5309.5376 | 0 | 0 | 0 | 0 | 3633.8627 | 468281.2737 | 3633.8627
OfL-w14-v14-VRF_HP_OAU1 | OfL | CZ14 | 14 | VRF_HP_OAU1 | 623.8884 | 1786588.875 | 500422.4062 | 0 | 883691.5 | 15519.7695 | 293693.8125 | 0 | 213.4769 | 93049.2109 | 0 | 0 | 0 | 0 | 2893.9674 | 0 | 0 | 2893.9674 | 3123.2159 | 5130.7285 | -5309.5376 | 0 | 0 | 0 | 0 | 3123.2159 | 402476.2698 | 3123.2159
OfL-w14-v14-VRF_HP_OAU2 | OfL | CZ14 | 14 | VRF_HP_OAU2 | 589.3152 | 1750221.125 | 500422.4062 | 0 | 883691.5 | 14082.0527 | 258765.4531 | 0 | 213.4769 | 93048.1562 | 0 | 0 | 0 | 0 | 2893.9674 | 0 | 0 | 2893.9674 | 2841.0069 | 5130.7285 | -5309.5376 | 0 | 0 | 0 | 0 | 2841.0069 | 366109.139 | 2841.0069
OfL-w14-v14-VRF_HR_OAU0 | OfL | CZ14 | 14 | VRF_HR_OAU0 | 675.8004 | 1827628.875 | 500422.4062 | 0 | 883691.5 | 14496.6152 | 335208.5625 | 0 | 213.4769 | 93597.3281 | 0 | 0 | 0 | 0 | 2893.9405 | 0 | 0 | 2893.9405 | 3441.684 | 5175.8716 | -5355.1909 | 0 | 0 | 0 | 0 | 3441.684 | 443515.9827 | 3441.684
OfL-w14-v14-VRF_HR_OAU1 | OfL | CZ14 | 14 | VRF_HR_OAU1 | 615.2073 | 1766305.75 | 500422.4062 | 0 | 883691.5 | 12381.9404 | 276001.0625 | 0 | 213.4769 | 93596.5938 | 0 | 0 | 0 | 0 | 2893.9405 | 0 | 0 | 2893.9405 | 2965.8183 | 5175.8716 | -5355.1909 | 0 | 0 | 0 | 0 | 2965.8183 | 382193.0735 | 2965.8183
OfL-w14-v14-VRF_HR_OAU2 | OfL | CZ14 | 14 | VRF_HR_OAU2 | 581.7066 | 1732262.25 | 500422.4062 | 0 | 883691.5 | 11191.0254 | 243149.4219 | 0 | 213.4769 | 93596.1328 | 0 | 0 | 0 | 0 | 2893.9405 | 0 | 0 | 2893.9405 | 2701.6444 | 5175.8716 | -5355.1909 | 0 | 0 | 0 | 0 | 2701.6444 | 348150.0569 | 2701.6444
EPr-w14-v14-AC_S1Std | EPr | CZ14 | 14 | AC_S1Std | 224.6312 | 359812 | 133157.6562 | 0 | 99493.7734 | 0 | 61683.8359 | 0 | 0 | 65476.7266 | 0 | 0 | 0 | 0 | 10526.1798 | 110.3944 | 8267.5168 | 2148.2691 | 1813.5176 | 1968.4746 | -4336.9341 | 0.22927 | 0 | 6 | 0 | 1813.5176 | 127160.5625 | 986.766
EPr-w14-v14-AC_S0Std | EPr | CZ14 | 14 | AC_S0Std | 224.6318 | 365205.6562 | 133157.6562 | 0 | 99493.7734 | 0 | 67077.375 | 0 | 0 | 65476.8594 | 0 | 0 | 0 | 0 | 10526.0557 | 110.3944 | 8267.3939 | 2148.2686 | 1855.3603 | 1968.4749 | -4336.9346 | 0.22927 | 0 | 6 | 0 | 1855.3603 | 132554.2344 | 1028.6209
EPr-w14-v14-AC_SHi | EPr | CZ14 | 14 | AC_SHi | 194.8091 | 327148.4062 | 133157.6562 | 0 | 99493.7734 | 0 | 48161.5898 | 0 | 0 | 46335.625 | 0 | 0 | 0 | 0 | 10583.3229 | 110.3944 | 8324.4973 | 2148.4304 | 1565.7481 | 1948.0225 | -3406.8865 | 0.15285 | 0 | 4 | 0 | 1565.7481 | 94497.2148 | 733.2984
EPr-w14-v14-AC_EStd | EPr | CZ14 | 14 | AC_EStd | 241.3034 | 363268.3438 | 133157.6562 | 0 | 99493.7734 | 0 | 66530.0234 | 0 | 0 | 64087.1602 | 0 | 0 | 0 | 0 | 10286.3418 | 110.3944 | 8027.5354 | 2148.4072 | 1816.3429 | 1991.6569 | -3472.4856 | 0.26748 | 0 | 7 | 0 | 1816.3429 | 130617.1836 | 1013.5893
EPr-w14-v14-AC_EHi | EPr | CZ14 | 14 | AC_EHi | 216.4572 | 351699.5 | 133157.6562 | 0 | 99493.7734 | 0 | 54961.1602 | 0 | 0 | 64087.1602 | 0 | 0 | 0 | 0 | 10286.3418 | 110.3944 | 8027.5354 | 2148.4072 | 1726.5685 | 1991.6569 | -3472.4856 | 0.26748 | 0 | 7 | 0 | 1726.5685 | 119048.3203 | 923.815
EPr-w14-v14-PVAV_Std | EPr | CZ14 | 14 | PVAV_Std | 238.6955 | 361713.1875 | 133157.6562 | 0 | 99493.7734 | 227.8397 | 77379.1094 | 0 | 516.4291 | 50938.2812 | 0 | 0 | 0 | 0 | 10590.3053 | 110.3944 | 8330.5222 | 2149.3877 | 1834.5707 | 2063.2412 | -1658.5647 | 0.22927 | 0 | 6 | 0 | 1834.5707 | 129061.6594 | 1001.5185
EPr-w14-v14-PVAV_Hi | EPr | CZ14 | 14 | PVAV_Hi | 203.9616 | 342584.5312 | 133157.6562 | 0 | 99493.7734 | 446.3506 | 59526.7109 | 0 | 535.7422 | 49424.2109 | 0 | 0 | 0 | 0 | 10022.9062 | 110.3944 | 7763.0349 | 2149.4768 | 1629.3837 | 2058.7603 | -1620.5657 | 0.15285 | 0 | 3 | 1 | 1629.3837 | 109933.0147 | 853.0802
EPr-w14-v14-VRF_HP_OAU0 | EPr | CZ14 | 14 | VRF_HP_OAU0 | 223.7777 | 399336.9375 | 133157.6562 | 0 | 99493.7734 | 48931.707 | 64941.6094 | 0 | 0 | 52812.1016 | 0 | 0 | 0 | 0 | 2258.3733 | 110.3944 | 0 | 2147.979 | 1293.4788 | 1600.3125 | -1655.2233 | 0.19106 | 0 | 5 | 0 | 1293.4788 | 166685.418 | 1293.4788
EPr-w14-v14-VRF_HP_OAU1 | EPr | CZ14 | 14 | VRF_HP_OAU1 | 208.0271 | 387144.7812 | 133157.6562 | 0 | 99493.7734 | 44394.8828 | 57286.375 | 0 | 0 | 52812.1016 | 0 | 0 | 0 | 0 | 2258.3733 | 110.3944 | 0 | 2147.979 | 1198.8685 | 1600.3125 | -1655.2233 | 0.19106 | 0 | 5 | 0 | 1198.8685 | 154493.3594 | 1198.8685
EPr-w14-v14-VRF_HP_OAU2 | EPr | CZ14 | 14 | VRF_HP_OAU2 | 195.1109 | 376766.4375 | 133157.6562 | 0 | 99493.7734 | 40368.8008 | 50948.6914 | 0 | 0 | 52797.6914 | 0 | 0 | 0 | 0 | 2258.3733 | 110.3944 | 0 | 2147.979 | 1118.3338 | 1598.9844 | -1653.847 | 0.19106 | 0 | 5 | 0 | 1118.3338 | 144115.1836 | 1118.3338
EPr-w14-v14-VRF_HR_OAU0 | EPr | CZ14 | 14 | VRF_HR_OAU0 | 211.9917 | 386677.9375 | 133157.6562 | 0 | 99493.7734 | 42206.1797 | 59179.4922 | 0 | 0 | 52640.7305 | 0 | 0 | 0 | 0 | 2258.3632 | 110.3944 | 0 | 2147.969 | 1195.2449 | 1589.5099 | -1643.9536 | 0.22927 | 0 | 6 | 0 | 1195.2449 | 154026.4023 | 1195.2449
EPr-w14-v14-VRF_HR_OAU1 | EPr | CZ14 | 14 | VRF_HR_OAU1 | 197.976 | 375673.25 | 133157.6562 | 0 | 99493.7734 | 38190.0156 | 52280.043 | 0 | 0 | 52551.957 | 0 | 0 | 0 | 0 | 2258.3632 | 110.3944 | 0 | 2147.969 | 1109.8508 | 1583.9095 | -1638.125 | 0.22927 | 0 | 6 | 0 | 1109.8508 | 143022.0156 | 1109.8508
EPr-w14-v14-VRF_HR_OAU2 | EPr | CZ14 | 14 | VRF_HR_OAU2 | 186.3643 | 366304.8125 | 133157.6562 | 0 | 99493.7734 | 34640.3984 | 46461.2031 | 0 | 0 | 52551.957 | 0 | 0 | 0 | 0 | 2258.3632 | 110.3944 | 0 | 2147.969 | 1037.1516 | 1583.9095 | -1638.125 | 0.22927 | 0 | 6 | 0 | 1037.1516 | 133653.5586 | 1037.1516
Htl-w14-v14-FPFC_1 | Htl | CZ14 | 14 | FPFC_1 | 720.6107 | 3993126.5 | 566447.625 | 0 | 1692748 | 9986.5039 | 805305.9375 | 11591.7168 | 314071.5 | 592975.1875 | 0 | 0 | 0 | 0 | 166317.4451 | 0 | 129295.7286 | 37021.7984 | 26294.9245 | 9192.6377 | -18363.2383 | 0.10273 | 0 | 9 | 0 | 26294.9245 | 1722339.1289 | 13365.3516
Htl-w14-v14-FPFC_2 | Htl | CZ14 | 14 | FPFC_2 | 660.2393 | 3796550.25 | 566447.625 | 0 | 1692748 | 22878.4531 | 576440.75 | 29205.3047 | 313796.7812 | 595033.25 | 0 | 0 | 0 | 0 | 143005.5424 | 0 | 105983.703 | 37021.8445 | 22301.6084 | 9192.6377 | -18363.2383 | 0.11414 | 0 | 9 | 1 | 22301.6084 | 1508149.2344 | 11703.2381
Htl-w14-v14-VRF_HP_OAU0 | Htl | CZ14 | 14 | VRF_HP_OAU0 | 969.8849 | 4450075 | 566447.625 | 0 | 1692748 | 861551 | 855370.5625 | 0 | 1121.6216 | 472836.0938 | 0 | 0 | 0 | 0 | 37021.6678 | 0 | 0 | 37021.6678 | 17001.2232 | 8326.5029 | -8564.9307 | 0.60495 | 0 | 53 | 0 | 17001.2232 | 2190879.2778 | 17001.2232
Htl-w14-v14-VRF_HP_OAU1 | Htl | CZ14 | 14 | VRF_HP_OAU1 | 881.8231 | 4234600.5 | 566447.625 | 0 | 1692748 | 769925.125 | 731521.5 | 0 | 1121.6216 | 472836.0938 | 0 | 0 | 0 | 0 | 37021.6678 | 0 | 0 | 37021.6678 | 15329.1377 | 8326.5 | -8564.9287 | 0.60495 | 0 | 53 | 0 | 15329.1377 | 1975404.3403 | 15329.1377
Htl-w14-v14-VRF_HP_OAU2 | Htl | CZ14 | 14 | VRF_HP_OAU2 | 815.5021 | 4066605 | 566447.625 | 0 | 1692748 | 694884.125 | 638567.8125 | 0 | 1121.6216 | 472836.0938 | 0 | 0 | 0 | 0 | 37021.6678 | 0 | 0 | 37021.6678 | 14025.4989 | 8326.5039 | -8564.9326 | 0.60495 | 0 | 53 | 0 | 14025.4989 | 1807409.6528 | 14025.4989
Htl-w14-v14-VRF_HR_OAU0 | Htl | CZ14 | 14 | VRF_HR_OAU0 | 953.0786 | 4302436.5 | 566447.625 | 0 | 1692748 | 770307.125 | 800802.75 | 0 | 1121.6216 | 471008.7188 | 0 | 0 | 0 | 0 | 37021.591 | 0 | 0 | 37021.591 | 15855.5441 | 8253.0215 | -8488.332 | 1.0273 | 0 | 85 | 5 | 15855.5441 | 2043240.2153 | 15855.5441
Htl-w14-v14-VRF_HR_OAU1 | Htl | CZ14 | 14 | VRF_HR_OAU1 | 865.8883 | 4100431 | 566447.625 | 0 | 1692748 | 686159.1875 | 682940.4375 | 0 | 1121.6216 | 471013.1875 | 0 | 0 | 0 | 0 | 37021.591 | 0 | 0 | 37021.591 | 14287.9792 | 8244.3516 | -8479.3379 | 1.0273 | 0 | 85 | 5 | 14287.9792 | 1841234.4341 | 14287.9792
Htl-w14-v14-VRF_HR_OAU2 | Htl | CZ14 | 14 | VRF_HR_OAU2 | 800.2811 | 3943810 | 566447.625 | 0 | 1692748 | 616578.9375 | 595898.375 | 0 | 1121.6216 | 471014.625 | 0 | 0 | 0 | 0 | 37021.591 | 0 | 0 | 37021.591 | 13072.6012 | 8241.9414 | -8476.8379 | 1.0273 | 0 | 85 | 5 | 13072.6012 | 1684613.5591 | 13072.6012
OfS-w15-v14-AC_S1Std | OfS | CZ15 | 14 | AC_S1Std | 51.5033 | 131345.1719 | 31593.9805 | 0 | 50648.0078 | 0 | 35157.2695 | 0 | 0 | 13945.9746 | 0 | 0 | 0 | 0 | 153.4025 | 0 | 6.863 | 146.5395 | 381.7275 | 417.968 | -511.2751 | 0 | 0 | 0 | 0 | 381.7275 | 49103.2441 | 381.0412
OfS-w15-v14-AC_S0Std | OfS | CZ15 | 14 | AC_S0Std | 51.5032 | 135503.5312 | 31593.9805 | 0 | 50648.0078 | 0 | 39315.5938 | 0 | 0 | 13946.0361 | 0 | 0 | 0 | 0 | 153.3781 | 0 | 6.8393 | 146.5388 | 413.9942 | 417.9679 | -511.2749 | 0 | 0 | 0 | 0 | 413.9942 | 53261.6299 | 413.3102
OfS-w15-v14-AC_SHi | OfS | CZ15 | 14 | AC_SHi | 44.1395 | 116390.2969 | 31593.9805 | 0 | 50648.0078 | 0 | 27055.5156 | 0 | 0 | 7092.8667 | 0 | 0 | 0 | 0 | 156.0479 | 0 | 9.4278 | 146.6202 | 265.9342 | 422.8834 | -371.5148 | 0 | 0 | 0 | 0 | 265.9342 | 34148.3823 | 264.9914
OfS-w15-v14-AC_EStd | OfS | CZ15 | 14 | AC_EStd | 52.9861 | 130253.7188 | 31593.9805 | 0 | 50648.0078 | 0 | 36564.5586 | 0 | 0 | 11447.2773 | 0 | 0 | 0 | 0 | 154.0271 | 0 | 7.4214 | 146.6057 | 373.314 | 431.2338 | -366.8997 | 0 | 0 | 0 | 0 | 373.314 | 48011.8359 | 372.5718
OfS-w15-v14-AC_EHi | OfS | CZ15 | 14 | AC_EHi | 47.9626 | 123895.5312 | 31593.9805 | 0 | 50648.0078 | 0 | 30206.375 | 0 | 0 | 11447.2773 | 0 | 0 | 0 | 0 | 154.0271 | 0 | 7.4214 | 146.6057 | 323.9745 | 431.2338 | -366.8997 | 0 | 0 | 0 | 0 | 323.9745 | 41653.6523 | 323.2323
OfS-w15-v14-PVAV_Std | OfS | CZ15 | 14 | PVAV_Std | 54.4044 | 134846.8594 | 31593.9805 | 0 | 50648.0078 | 2.3899 | 44011.5977 | 0 | 57.3994 | 8533.6299 | 0 | 0 | 0 | 0 | 178.0438 | 0 | 31.0098 | 147.034 | 411.3159 | 0 | 0 | 0 | 0 | 0 | 0 | 411.3159 | 52605.0169 | 408.2149
OfS-w15-v14-PVAV_Hi | OfS | CZ15 | 14 | PVAV_Hi | 46.7868 | 124254.9688 | 31593.9805 | 0 | 50648.0078 | 4.6847 | 33299.4023 | 0 | 57.5177 | 8651.498 | 0 | 0 | 0 | 0 | 165.0486 | 0 | 18.0164 | 147.0321 | 327.8233 | 0 | 0 | 0 | 0 | 0 | 0 | 327.8233 | 42013.1028 | 326.0217
OfS-w15-v14-VRF_HP_OAU0 | OfS | CZ15 | 14 | VRF_HP_OAU0 | 48.7577 | 125929.4453 | 31593.9805 | 0 | 50648.0078 | 135.4584 | 37452.6797 | 0 | 0 | 6099.3989 | 0 | 0 | 0 | 0 | 146.5189 | 0 | 0 | 146.5189 | 339.0153 | 375.561 | -391.4367 | 0 | 0 | 0 | 0 | 339.0153 | 43687.537 | 339.0153
OfS-w15-v14-VRF_HP_OAU1 | OfS | CZ15 | 14 | VRF_HP_OAU1 | 45.5557 | 121444.0391 | 31593.9805 | 0 | 50648.0078 | 122.2959 | 32980.4219 | 0 | 0 | 6099.3989 | 0 | 0 | 0 | 0 | 146.5189 | 0 | 0 | 146.5189 | 304.2084 | 375.561 | -391.4367 | 0 | 0 | 0 | 0 | 304.2084 | 39202.1167 | 304.2084
OfS-w15-v14-VRF_HP_OAU2 | OfS | CZ15 | 14 | VRF_HP_OAU2 | 42.8732 | 117675.9844 | 31593.9805 | 0 | 50648.0078 | 110.7222 | 29223.9648 | 0 | 0 | 6099.3989 | 0 | 0 | 0 | 0 | 146.5189 | 0 | 0 | 146.5189 | 274.9685 | 375.561 | -391.4367 | 0 | 0 | 0 | 0 | 274.9685 | 35434.086 | 274.9685
OfS-w15-v14-VRF_HR_OAU0 | OfS | CZ15 | 14 | VRF_HR_OAU0 | 47.0856 | 123111.0078 | 31593.9805 | 0 | 50648.0078 | 102.1707 | 34708.207 | 0 | 0 | 6058.7607 | 0 | 0 | 0 | 0 | 146.4931 | 0 | 0 | 146.4931 | 317.1445 | 370.9011 | -386.6328 | 0 | 0 | 0 | 0 | 317.1445 | 40869.1384 | 317.1445
OfS-w15-v14-VRF_HR_OAU1 | OfS | CZ15 | 14 | VRF_HR_OAU1 | 44.0965 | 118965.2812 | 31593.9805 | 0 | 50648.0078 | 91.7551 | 30572.8828 | 0 | 0 | 6058.7607 | 0 | 0 | 0 | 0 | 146.4931 | 0 | 0 | 146.4931 | 284.9736 | 370.9011 | -386.6328 | 0 | 0 | 0 | 0 | 284.9736 | 36723.3986 | 284.9736
OfS-w15-v14-VRF_HR_OAU2 | OfS | CZ15 | 14 | VRF_HR_OAU2 | 41.5906 | 115476.3438 | 31593.9805 | 0 | 50648.0078 | 82.6669 | 27093.0508 | 0 | 0 | 6058.7607 | 0 | 0 | 0 | 0 | 146.4931 | 0 | 0 | 146.4931 | 257.8996 | 370.9011 | -386.6328 | 0 | 0 | 0 | 0 | 257.8996 | 33234.4784 | 257.8996
OfL-w15-v14-FPFC_1 | OfL | CZ15 | 14 | FPFC_1 | 579.7179 | 2148958 | 500422.4062 | 0 | 883691.5 | 85.1561 | 514129.1875 | 6973.3291 | 154702 | 88954.0547 | 0 | 0 | 0 | 0 | 3475.7283 | 0 | 1085.7515 | 2389.9766 | 5989.6494 | 5425.1206 | -9214.7119 | 0 | 0 | 0 | 0 | 5989.6494 | 757870.3983 | 5881.0743
OfL-w15-v14-FPFC_2 | OfL | CZ15 | 14 | FPFC_2 | 529.7973 | 1998094.375 | 500422.4062 | 0 | 883691.5 | 166.5934 | 343480.0312 | 26689.9258 | 154691.5625 | 88952.8594 | 0 | 0 | 0 | 0 | 2886.736 | 0 | 496.75 | 2389.9858 | 4607.0535 | 5425.1206 | -9214.7119 | 0 | 0 | 0 | 0 | 4607.0535 | 587291.0465 | 4557.3785
OfL-w15-v14-VRF_HP_OAU0 | OfL | CZ15 | 14 | VRF_HP_OAU0 | 760.0823 | 2104329.25 | 500422.4062 | 0 | 883691.5 | 1261.5098 | 615189.25 | 0 | 213.4769 | 103551.375 | 0 | 0 | 0 | 0 | 2389.2782 | 0 | 0 | 2389.2782 | 5588.8731 | 6025.1582 | -6276.9175 | 0 | 0 | 0 | 0 | 5588.8731 | 720215.6116 | 5588.8731
OfL-w15-v14-VRF_HP_OAU1 | OfL | CZ15 | 14 | VRF_HP_OAU1 | 684.9832 | 1994615.75 | 500422.4062 | 0 | 883691.5 | 1076.8361 | 505660.6875 | 0 | 213.4769 | 103551.3672 | 0 | 0 | 0 | 0 | 2389.2782 | 0 | 0 | 2389.2782 | 4737.4984 | 6025.1582 | -6276.9175 | 0 | 0 | 0 | 0 | 4737.4984 | 610502.3676 | 4737.4984
OfL-w15-v14-VRF_HP_OAU2 | OfL | CZ15 | 14 | VRF_HP_OAU2 | 643.7446 | 1934245.25 | 500422.4062 | 0 | 883691.5 | 968.0884 | 445399.2188 | 0 | 213.4769 | 103551.3594 | 0 | 0 | 0 | 0 | 2389.2782 | 0 | 0 | 2389.2782 | 4269.0254 | 6025.1582 | -6276.9175 | 0 | 0 | 0 | 0 | 4269.0254 | 550132.1434 | 4269.0254
OfL-w15-v14-VRF_HR_OAU0 | OfL | CZ15 | 14 | VRF_HR_OAU0 | 712.952 | 2047599 | 500422.4062 | 0 | 883691.5 | 1001.5587 | 557905.125 | 0 | 213.4769 | 104364.9062 | 0 | 0 | 0 | 0 | 2389.241 | 0 | 0 | 2389.241 | 5148.6441 | 6095.5254 | -6350.4404 | 0 | 0 | 0 | 0 | 5148.6441 | 663485.0668 | 5148.6441
OfL-w15-v14-VRF_HR_OAU1 | OfL | CZ15 | 14 | VRF_HR_OAU1 | 646.7087 | 1948247.75 | 500422.4062 | 0 | 883691.5 | 849.2599 | 458706.8125 | 0 | 213.4769 | 104364.9062 | 0 | 0 | 0 | 0 | 2389.241 | 0 | 0 | 2389.241 | 4377.6834 | 6095.5254 | -6350.4404 | 0 | 0 | 0 | 0 | 4377.6834 | 564134.4555 | 4377.6834
OfL-w15-v14-VRF_HR_OAU2 | OfL | CZ15 | 14 | VRF_HR_OAU2 | 610.2761 | 1893685.25 | 500422.4062 | 0 | 883691.5 | 761.2487 | 404232.3438 | 0 | 213.4769 | 104364.9062 | 0 | 0 | 0 | 0 | 2389.241 | 0 | 0 | 2389.241 | 3954.2785 | 6095.5254 | -6350.4404 | 0 | 0 | 0 | 0 | 3954.2785 | 509571.9755 | 3954.2785
EPr-w15-v14-AC_S1Std | EPr | CZ15 | 14 | AC_S1Std | 264.7997 | 445083.875 | 133157.6562 | 0 | 99493.7734 | 0 | 138755.4219 | 0 | 0 | 73677.4688 | 0 | 0 | 0 | 0 | 3686.0835 | 110.3944 | 1798.6803 | 1777.0083 | 1828.3473 | 2251.6873 | -3783.5581 | 0.91708 | 0 | 24 | 0 | 1828.3473 | 212432.8906 | 1648.4792
EPr-w15-v14-AC_S0Std | EPr | CZ15 | 14 | AC_S0Std | 264.7997 | 453170.625 | 133157.6562 | 0 | 99493.7734 | 0 | 146842.1875 | 0 | 0 | 73677.4922 | 0 | 0 | 0 | 0 | 3685.9978 | 110.3944 | 1798.5955 | 1777.008 | 1891.0923 | 2251.6873 | -3783.5581 | 0.91708 | 0 | 24 | 0 | 1891.0923 | 220519.6797 | 1711.2327
EPr-w15-v14-AC_SHi | EPr | CZ15 | 14 | AC_SHi | 225.4996 | 392973.75 | 133157.6562 | 0 | 99493.7734 | 0 | 108363.0703 | 0 | 0 | 51959.5938 | 0 | 0 | 0 | 0 | 3743.6826 | 110.3944 | 1856.1144 | 1777.1731 | 1429.7153 | 2219.3459 | -2892.5237 | 0.68781 | 0 | 18 | 0 | 1429.7153 | 160322.6641 | 1244.1039
EPr-w15-v14-AC_EStd | EPr | CZ15 | 14 | AC_EStd | 287.2897 | 458963.5 | 133157.6562 | 0 | 99493.7734 | 0 | 150785.8281 | 0 | 0 | 75526.6094 | 0 | 0 | 0 | 0 | 3608.4493 | 110.3944 | 1720.9064 | 1777.1488 | 1928.2752 | 2299.7358 | -2958.9509 | 0.95529 | 0 | 25 | 0 | 1928.2752 | 226312.4375 | 1756.1845
EPr-w15-v14-AC_EHi | EPr | CZ15 | 14 | AC_EHi | 255.1351 | 432743.375 | 133157.6562 | 0 | 99493.7734 | 0 | 124565.7734 | 0 | 0 | 75526.6094 | 0 | 0 | 0 | 0 | 3608.4493 | 110.3944 | 1720.9064 | 1777.1488 | 1724.8075 | 2299.7358 | -2958.9509 | 0.95529 | 0 | 25 | 0 | 1724.8075 | 200092.3828 | 1552.7169
EPr-w15-v14-PVAV_Std | EPr | CZ15 | 14 | PVAV_Std | 277.7099 | 461417.4062 | 133157.6562 | 0 | 99493.7734 | 42.2927 | 169068.875 | 0 | 89.2623 | 59566.0391 | 0 | 0 | 0 | 0 | 3840.3606 | 110.3944 | 1951.7909 | 1778.1744 | 1970.4069 | 2329.5664 | -1428.0156 | 0.91708 | 0 | 24 | 0 | 1970.4069 | 228766.4691 | 1775.2278
EPr-w15-v14-PVAV_Hi | EPr | CZ15 | 14 | PVAV_Hi | 233.3111 | 420406.3438 | 133157.6562 | 0 | 99493.7734 | 73.4222 | 129752.4297 | 0 | 91.6718 | 57837.6719 | 0 | 0 | 0 | 0 | 3822.8771 | 110.3944 | 1934.2947 | 1778.1878 | 1650.4098 | 2311.177 | -1381.9084 | 0.34391 | 0 | 9 | 0 | 1650.4098 | 187755.1956 | 1456.9803
EPr-w15-v14-VRF_HP_OAU0 | EPr | CZ15 | 14 | VRF_HP_OAU0 | 277.119 | 442620.75 | 133157.6562 | 0 | 99493.7734 | 9989.2266 | 144554.9688 | 0 | 0 | 55425.5977 | 0 | 0 | 0 | 0 | 1887.0022 | 110.3944 | 0 | 1776.6077 | 1629.3656 | 1844.204 | -1924.9391 | 0.42033 | 0 | 11 | 0 | 1629.3656 | 209969.793 | 1629.3656
EPr-w15-v14-VRF_HP_OAU1 | EPr | CZ15 | 14 | VRF_HP_OAU1 | 254.8702 | 424414.9688 | 133157.6562 | 0 | 99493.7734 | 9027.2246 | 127311.2109 | 0 | 0 | 55425.582 | 0 | 0 | 0 | 0 | 1887.0022 | 110.3944 | 0 | 1776.6077 | 1488.0888 | 1844.204 | -1924.9391 | 0.42033 | 0 | 11 | 0 | 1488.0888 | 191764.0176 | 1488.0888
EPr-w15-v14-VRF_HP_OAU2 | EPr | CZ15 | 14 | VRF_HP_OAU2 | 236.2355 | 409086.0625 | 133157.6562 | 0 | 99493.7734 | 8181.5005 | 112828.125 | 0 | 0 | 55425.5586 | 0 | 0 | 0 | 0 | 1887.0022 | 110.3944 | 0 | 1776.6077 | 1369.137 | 1844.204 | -1924.9391 | 0.42033 | 0 | 11 | 0 | 1369.137 | 176435.1841 | 1369.137
EPr-w15-v14-VRF_HR_OAU0 | EPr | CZ15 | 14 | VRF_HR_OAU0 | 253.1359 | 428500.75 | 133157.6562 | 0 | 99493.7734 | 8381.4561 | 132442.3438 | 0 | 0 | 55025.9609 | 0 | 0 | 0 | 0 | 1886.9835 | 110.3944 | 0 | 1776.589 | 1519.7941 | 1819.7385 | -1899.5409 | 0.42033 | 0 | 11 | 0 | 1519.7941 | 195849.7607 | 1519.7941
EPr-w15-v14-VRF_HR_OAU1 | EPr | CZ15 | 14 | VRF_HR_OAU1 | 233.9241 | 411868.5 | 133157.6562 | 0 | 99493.7734 | 7532.2246 | 116659.3438 | 0 | 0 | 55025.9492 | 0 | 0 | 0 | 0 | 1886.9835 | 110.3944 | 0 | 1776.589 | 1390.7279 | 1819.7385 | -1899.5409 | 0.42033 | 0 | 11 | 0 | 1390.7279 | 179217.5176 | 1390.7279
EPr-w15-v14-VRF_HR_OAU2 | EPr | CZ15 | 14 | VRF_HR_OAU2 | 217.8033 | 397890.625 | 133157.6562 | 0 | 99493.7734 | 6789.7158 | 103424.0781 | 0 | 0 | 55025.8828 | 0 | 0 | 0 | 0 | 1886.9835 | 110.3944 | 0 | 1776.589 | 1282.2599 | 1819.7385 | -1899.5409 | 0.42033 | 0 | 11 | 0 | 1282.2599 | 165239.6768 | 1282.2599
Htl-w15-v14-FPFC_1 | Htl | CZ15 | 14 | FPFC_1 | 840.5673 | 5113226 | 566447.625 | 0 | 1692748 | 3915.4241 | 1618326 | 19464.627 | 517135.625 | 695187.625 | 0 | 0 | 0 | 0 | 78074.6906 | 0 | 49923.0259 | 28151.6493 | 26988.5245 | 10996.9922 | -19054.5078 | 0 | 0 | 0 | 0 | 26988.5245 | 2834564.6741 | 21996.2219
Htl-w15-v14-FPFC_2 | Htl | CZ15 | 14 | FPFC_2 | 744.433 | 4597772 | 566447.625 | 0 | 1692748 | 11477.0117 | 1047622.9375 | 72921.4688 | 511222.7812 | 695331.9375 | 0 | 0 | 0 | 0 | 67067.7709 | 0 | 38916.1856 | 28151.5699 | 21473.0988 | 10996.9922 | -19054.5078 | 0 | 0 | 0 | 0 | 21473.0988 | 2265654.668 | 17581.4802
Htl-w15-v14-VRF_HP_OAU0 | Htl | CZ15 | 14 | VRF_HP_OAU0 | 1150.7415 | 4788531 | 566447.625 | 0 | 1692748 | 255011.75 | 1751281.375 | 0 | 1121.6216 | 521920.1875 | 0 | 0 | 0 | 0 | 28150.0083 | 0 | 0 | 28150.0083 | 19627.6391 | 9895.9072 | -10259.6416 | 0.19404 | 0 | 17 | 0 | 19627.6391 | 2529334.9341 | 19627.6391
Htl-w15-v14-VRF_HP_OAU1 | Htl | CZ15 | 14 | VRF_HP_OAU1 | 1036.9456 | 4507421.5 | 566447.625 | 0 | 1692748 | 227244.0156 | 1497939.25 | 0 | 1121.6216 | 521920.1875 | 0 | 0 | 0 | 0 | 28150.0083 | 0 | 0 | 28150.0083 | 17446.2266 | 9895.9072 | -10259.6416 | 0.19404 | 0 | 17 | 0 | 17446.2266 | 2248225.0747 | 17446.2266
Htl-w15-v14-VRF_HP_OAU2 | Htl | CZ15 | 14 | VRF_HP_OAU2 | 950.6299 | 4294308 | 566447.625 | 0 | 1692748 | 204705.5312 | 1307364.375 | 0 | 1121.6216 | 521920.1875 | 0 | 0 | 0 | 0 | 28150.0083 | 0 | 0 | 28150.0083 | 15792.4669 | 9895.9072 | -10259.6416 | 0.19404 | 0 | 17 | 0 | 15792.4669 | 2035111.7153 | 15792.4669
Htl-w15-v14-VRF_HR_OAU0 | Htl | CZ15 | 14 | VRF_HR_OAU0 | 1101.6143 | 4651532 | 566447.625 | 0 | 1692748 | 227777 | 1644025.75 | 0 | 1121.6216 | 519410.4062 | 0 | 0 | 0 | 0 | 28149.8778 | 0 | 0 | 28149.8778 | 18564.5179 | 10043.4971 | -10412.4775 | 0.84465 | 0 | 71 | 3 | 18564.5179 | 2392334.7778 | 18564.5179
Htl-w15-v14-VRF_HR_OAU1 | Htl | CZ15 | 14 | VRF_HR_OAU1 | 994.0775 | 4387135.5 | 566447.625 | 0 | 1692748 | 202366.0938 | 1405040.625 | 0 | 1121.6216 | 519410.4062 | 0 | 0 | 0 | 0 | 28149.8778 | 0 | 0 | 28149.8778 | 16512.8047 | 10043.4971 | -10412.4775 | 0.84465 | 0 | 71 | 3 | 16512.8047 | 2127938.7466 | 16512.8047
Htl-w15-v14-VRF_HR_OAU2 | Htl | CZ15 | 14 | VRF_HR_OAU2 | 912.9232 | 4186869.5 | 566447.625 | 0 | 1692748 | 181316.4219 | 1225824.625 | 0 | 1121.6216 | 519410.4062 | 0 | 0 | 0 | 0 | 28149.8778 | 0 | 0 | 28149.8778 | 14958.7431 | 10043.4971 | -10412.4775 | 0.84465 | 0 | 71 | 3 | 14958.7431 | 1927673.0747 | 14958.7431
OfS-w16-v14-AC_S1Std | OfS | CZ16 | 14 | AC_S1Std | 33.2295 | 96256.7969 | 31593.9805 | 0 | 50648.0078 | 0 | 5963.1187 | 0 | 0 | 8051.7939 | 0 | 0 | 0 | 0 | 1275.5944 | 0 | 1078.1222 | 197.4723 | 216.5679 | 214.642 | -346.3066 | 0 | 0 | 0 | 0 | 216.5679 | 14014.9126 | 108.7557
OfS-w16-v14-AC_S0Std | OfS | CZ16 | 14 | AC_S0Std | 33.2316 | 98746.3203 | 31593.9805 | 0 | 50648.0078 | 0 | 8455.2637 | 0 | 0 | 8049.1519 | 0 | 0 | 0 | 0 | 1275.216 | 0 | 1077.7452 | 197.4711 | 235.8488 | 214.654 | -346.2274 | 0 | 0 | 0 | 0 | 235.8488 | 16504.4155 | 128.0743
OfS-w16-v14-AC_SHi | OfS | CZ16 | 14 | AC_SHi | 30.2233 | 91249.0547 | 31593.9805 | 0 | 50648.0078 | 0 | 4702.5288 | 0 | 0 | 4304.6289 | 0 | 0 | 0 | 0 | 1349.5381 | 0 | 1152.0232 | 197.5146 | 185.0979 | 213.2791 | -338.791 | 0 | 0 | 0 | 0 | 185.0979 | 9007.1577 | 69.8955
OfS-w16-v14-AC_EStd | OfS | CZ16 | 14 | AC_EStd | 34.1681 | 95439.2188 | 31593.9805 | 0 | 50648.0078 | 0 | 6563.9443 | 0 | 0 | 6633.3647 | 0 | 0 | 0 | 0 | 1316.2701 | 0 | 1118.7658 | 197.5042 | 214.2877 | 212.0183 | -335.3096 | 0 | 0 | 0 | 0 | 214.2877 | 13197.3091 | 102.4111
OfS-w16-v14-AC_EHi | OfS | CZ16 | 14 | AC_EHi | 32.1691 | 94297.8359 | 31593.9805 | 0 | 50648.0078 | 0 | 5422.5459 | 0 | 0 | 6633.3647 | 0 | 0 | 0 | 0 | 1316.2701 | 0 | 1118.7658 | 197.5042 | 205.4304 | 212.0183 | -335.3096 | 0 | 0 | 0 | 0 | 205.4304 | 12055.9106 | 93.5539
OfS-w16-v14-PVAV_Std | OfS | CZ16 | 14 | PVAV_Std | 36.356 | 95893.1016 | 31593.9805 | 0 | 50648.0078 | 76.2581 | 8732.4668 | 0 | 564.443 | 4277.9346 | 0 | 0 | 0 | 0 | 1288.1567 | 0 | 1090.8894 | 197.2673 | 215.0215 | 0 | 0 | 0 | 0 | 0 | 0 | 215.0215 | 13651.1025 | 105.9326
OfS-w16-v14-PVAV_Hi | OfS | CZ16 | 14 | PVAV_Hi | 33.1724 | 93926.4844 | 31593.9805 | 0 | 50648.0078 | 143.6925 | 6616.3975 | 0 | 580.4348 | 4343.9673 | 0 | 0 | 0 | 0 | 1047.5162 | 0 | 850.2291 | 197.287 | 175.6946 | 0 | 0 | 0 | 0 | 0 | 0 | 175.6946 | 11684.4921 | 90.6717
OfS-w16-v14-VRF_HP_OAU0 | OfS | CZ16 | 14 | VRF_HP_OAU0 | 32.096 | 104723.25 | 31593.9805 | 0 | 50648.0078 | 9451.457 | 8394.3145 | 0 | 0 | 4635.6191 | 0 | 0 | 0 | 0 | 197.4371 | 0 | 0 | 197.4371 | 174.4556 | 245.1844 | -251.177 | 0 | 0 | 0 | 0 | 174.4556 | 22481.3906 | 174.4556
OfS-w16-v14-VRF_HP_OAU1 | OfS | CZ16 | 14 | VRF_HP_OAU1 | 30.9271 | 102938.5156 | 31593.9805 | 0 | 50648.0078 | 8638.4824 | 7422.5234 | 0 | 0 | 4635.6191 | 0 | 0 | 0 | 0 | 197.4371 | 0 | 0 | 197.4371 | 160.6058 | 245.1844 | -251.177 | 0 | 0 | 0 | 0 | 160.6058 | 20696.625 | 160.6058
OfS-w16-v14-VRF_HP_OAU2 | OfS | CZ16 | 14 | VRF_HP_OAU2 | 29.8839 | 101389.5391 | 31593.9805 | 0 | 50648.0078 | 7910.0596 | 6601.958 | 0 | 0 | 4635.6191 | 0 | 0 | 0 | 0 | 197.4371 | 0 | 0 | 197.4371 | 148.5857 | 245.1844 | -251.177 | 0 | 0 | 0 | 0 | 148.5857 | 19147.6367 | 148.5857
OfS-w16-v14-VRF_HR_OAU0 | OfS | CZ16 | 14 | VRF_HR_OAU0 | 31.7224 | 102819.6172 | 31593.9805 | 0 | 50648.0078 | 8099.8477 | 7841.5029 | 0 | 0 | 4636.3755 | 0 | 0 | 0 | 0 | 197.4332 | 0 | 0 | 197.4332 | 159.6832 | 244.4382 | -250.4215 | 0 | 0 | 0 | 0 | 159.6832 | 20577.7261 | 159.6832
OfS-w16-v14-VRF_HR_OAU1 | OfS | CZ16 | 14 | VRF_HR_OAU1 | 30.5281 | 101204.3125 | 31593.9805 | 0 | 50648.0078 | 7375.354 | 6950.6934 | 0 | 0 | 4636.3755 | 0 | 0 | 0 | 0 | 197.4332 | 0 | 0 | 197.4332 | 147.1484 | 244.4382 | -250.4215 | 0 | 0 | 0 | 0 | 147.1484 | 18962.4229 | 147.1484
OfS-w16-v14-VRF_HR_OAU2 | OfS | CZ16 | 14 | VRF_HR_OAU2 | 29.3925 | 99799.1484 | 31593.9805 | 0 | 50648.0078 | 6721.5469 | 6199.3267 | 0 | 0 | 4636.3755 | 0 | 0 | 0 | 0 | 197.4332 | 0 | 0 | 197.4332 | 136.2443 | 244.4375 | -250.4208 | 0 | 0 | 0 | 0 | 136.2443 | 17557.249 | 136.2443
OfL-w16-v14-FPFC_1 | OfL | CZ16 | 14 | FPFC_1 | 467.7195 | 1681181.625 | 500422.4062 | 0 | 883691.5 | 883.6992 | 164914.1562 | 2527.6868 | 57166.9648 | 71576.8906 | 0 | 0 | 0 | 0 | 15106.4947 | 0 | 11781.5194 | 3324.9766 | 3463.7956 | 3136.2983 | -7236.2119 | 0 | 0 | 0 | 0 | 3463.7956 | 294541.7109 | 2285.6437
OfL-w16-v14-FPFC_2 | OfL | CZ16 | 14 | FPFC_2 | 443.6242 | 1639278 | 500422.4062 | 0 | 883691.5 | 1829.4857 | 120750.7344 | 4206.5615 | 56868.1797 | 71510.8594 | 0 | 0 | 0 | 0 | 11993.6832 | 0 | 8668.6176 | 3325.0646 | 2814.3056 | 3136.2983 | -7236.2119 | 0 | 0 | 0 | 0 | 2814.3056 | 250959.2592 | 1947.4439
OfL-w16-v14-VRF_HP_OAU0 | OfL | CZ16 | 14 | VRF_HP_OAU0 | 511.711 | 1706954.375 | 500422.4062 | 0 | 883691.5 | 81641.7188 | 160544.5781 | 0 | 213.4769 | 80442.1562 | 0 | 0 | 0 | 0 | 3324.8621 | 0 | 0 | 3324.8621 | 2505.2534 | 3988.2754 | -4087.4019 | 0 | 0 | 0 | 0 | 2505.2534 | 322841.93 | 2505.2534
OfL-w16-v14-VRF_HP_OAU1 | OfL | CZ16 | 14 | VRF_HP_OAU1 | 481.5192 | 1668351.75 | 500422.4062 | 0 | 883691.5 | 71202.4688 | 132381.3438 | 0 | 213.4769 | 80442.1562 | 0 | 0 | 0 | 0 | 3324.8621 | 0 | 0 | 3324.8621 | 2205.6981 | 3988.2754 | -4087.4019 | 0 | 0 | 0 | 0 | 2205.6981 | 284239.4456 | 2205.6981
OfL-w16-v14-VRF_HP_OAU2 | OfL | CZ16 | 14 | VRF_HP_OAU2 | 465.1384 | 1646619.5 | 500422.4062 | 0 | 883691.5 | 64986.0586 | 117049.1953 | 0 | 213.4769 | 80258.6641 | 0 | 0 | 0 | 0 | 3324.8624 | 0 | 0 | 3324.8624 | 2037.0574 | 3966.2437 | -4064.6692 | 0 | 0 | 0 | 0 | 2037.0574 | 262507.3948 | 2037.0574
OfL-w16-v14-VRF_HR_OAU0 | OfL | CZ16 | 14 | VRF_HR_OAU0 | 503.0822 | 1685797.5 | 500422.4062 | 0 | 883691.5 | 68250.1641 | 152240.1562 | 0 | 213.4769 | 80981.5156 | 0 | 0 | 0 | 0 | 3324.8531 | 0 | 0 | 3324.8531 | 2341.078 | 4011.9595 | -4110.7236 | 0 | 0 | 0 | 0 | 2341.078 | 301685.3128 | 2341.078
OfL-w16-v14-VRF_HR_OAU1 | OfL | CZ16 | 14 | VRF_HR_OAU1 | 473.6687 | 1650186.75 | 500422.4062 | 0 | 883691.5 | 59295.4297 | 125584.0781 | 0 | 213.4769 | 80981.5156 | 0 | 0 | 0 | 0 | 3324.8531 | 0 | 0 | 3324.8531 | 2064.7381 | 4011.9595 | -4110.7236 | 0 | 0 | 0 | 0 | 2064.7381 | 266074.5003 | 2064.7381
OfL-w16-v14-VRF_HR_OAU2 | OfL | CZ16 | 14 | VRF_HR_OAU2 | 457.3015 | 1629941.375 | 500422.4062 | 0 | 883691.5 | 53950.375 | 110683.8594 | 0 | 213.4769 | 80981.5156 | 0 | 0 | 0 | 0 | 3324.8531 | 0 | 0 | 3324.8531 | 1907.6348 | 4011.9629 | -4110.7275 | 0 | 0 | 0 | 0 | 1907.6348 | 245829.2269 | 1907.6348
EPr-w16-v14-AC_S1Std | EPr | CZ16 | 14 | AC_S1Std | 1.6302 | 290113.9062 | 133157.6562 | 0 | 99493.7734 | 0 | 12517.0273 | 0 | 0 | 44945.9648 | 0 | 0 | 0 | 0 | 21786.455 | 110.3944 | 19216.6131 | 2459.4446 | 2367.5741 | 953.5861 | -2852.7197 | 0.34391 | 0 | 9 | 0 | 2367.5741 | 57462.9922 | 445.9128
EPr-w16-v14-AC_S0Std | EPr | CZ16 | 14 | AC_S0Std | 1.6302 | 290770.4062 | 133157.6562 | 0 | 99493.7734 | 0 | 13174.2471 | 0 | 0 | 44945.2266 | 0 | 0 | 0 | 0 | 21786.4192 | 110.3944 | 19216.5824 | 2459.4445 | 2372.6654 | 953.5912 | -2852.6943 | 0.34391 | 0 | 9 | 0 | 2372.6654 | 58119.4736 | 451.0071
EPr-w16-v14-AC_SHi | EPr | CZ16 | 14 | AC_SHi | 1.6302 | 276966.1562 | 133157.6562 | 0 | 99493.7734 | 0 | 10052.9951 | 0 | 0 | 34262.125 | 0 | 0 | 0 | 0 | 22140.4902 | 110.3944 | 19570.5254 | 2459.5702 | 2300.9379 | 933.278 | -2855.7278 | 0.34391 | 0 | 9 | 0 | 2300.9379 | 44315.1201 | 343.8853
EPr-w16-v14-AC_EStd | EPr | CZ16 | 14 | AC_EStd | 1.6302 | 290939.625 | 133157.6562 | 0 | 99493.7734 | 0 | 14138.6797 | 0 | 0 | 44149.9844 | 0 | 0 | 0 | 0 | 21828.4109 | 110.3944 | 19258.4576 | 2459.5584 | 2378.1658 | 931.8419 | -2838.5942 | 0.38212 | 0 | 10 | 0 | 2378.1658 | 58288.6641 | 452.32
EPr-w16-v14-AC_EHi | EPr | CZ16 | 14 | AC_EHi | 1.6302 | 288481.0938 | 133157.6562 | 0 | 99493.7734 | 0 | 11680.1152 | 0 | 0 | 44149.9844 | 0 | 0 | 0 | 0 | 21828.4109 | 110.3944 | 19258.4576 | 2459.5584 | 2359.0873 | 931.8419 | -2838.5942 | 0.38212 | 0 | 10 | 0 | 2359.0873 | 55830.0996 | 433.2416
EPr-w16-v14-PVAV_Std | EPr | CZ16 | 14 | PVAV_Std | 1.6302 | 300650.2812 | 133157.6562 | 0 | 99493.7734 | 558.1039 | 18296.1562 | 0 | 1038.8339 | 48105.8398 | 0 | 0 | 0 | 0 | 21373.1264 | 110.3944 | 18802.6611 | 2460.0693 | 2407.9378 | 970.962 | -1111.8175 | 0.34391 | 0 | 9 | 0 | 2407.9378 | 67998.9339 | 527.6717
EPr-w16-v14-PVAV_Hi | EPr | CZ16 | 14 | PVAV_Hi | 1.6302 | 296207.1875 | 133157.6562 | 0 | 99493.7734 | 1013.3759 | 13997.2666 | 0 | 1102.9178 | 47442.4141 | 0 | 0 | 0 | 0 | 19861.1021 | 110.3944 | 17290.4166 | 2460.2931 | 2222.236 | 947.6235 | -1112.8776 | 0.076423 | 0 | 2 | 0 | 2222.236 | 63555.9744 | 493.1944
EPr-w16-v14-VRF_HP_OAU0 | EPr | CZ16 | 14 | VRF_HP_OAU0 | 1.6302 | 425960.4062 | 133157.6562 | 0 | 99493.7734 | 130255.8906 | 14242.6611 | 0 | 0 | 48810.3438 | 0 | 0 | 0 | 0 | 2569.5622 | 110.3944 | 0 | 2459.1682 | 1500.077 | 1105.1118 | -1132.5073 | 0 | 0 | 0 | 0 | 1500.077 | 193308.8955 | 1500.077
EPr-w16-v14-VRF_HP_OAU1 | EPr | CZ16 | 14 | VRF_HP_OAU1 | 1.6302 | 412711.375 | 133157.6562 | 0 | 99493.7734 | 118663.7031 | 12585.9766 | 0 | 0 | 48810.3438 | 0 | 0 | 0 | 0 | 2569.5622 | 110.3944 | 0 | 2459.1682 | 1397.2658 | 1105.1118 | -1132.5073 | 0 | 0 | 0 | 0 | 1397.2658 | 180060.0234 | 1397.2658
EPr-w16-v14-VRF_HP_OAU2 | EPr | CZ16 | 14 | VRF_HP_OAU2 | 1.6302 | 401133.25 | 133157.6562 | 0 | 99493.7734 | 108486.1406 | 11185.4697 | 0 | 0 | 48810.3438 | 0 | 0 | 0 | 0 | 2569.5622 | 110.3944 | 0 | 2459.1682 | 1307.42 | 1105.1118 | -1132.5073 | 0 | 0 | 0 | 0 | 1307.42 | 168481.9541 | 1307.42
EPr-w16-v14-VRF_HR_OAU0 | EPr | CZ16 | 14 | VRF_HR_OAU0 | 1.6302 | 407891.8438 | 133157.6562 | 0 | 99493.7734 | 113289.9844 | 13113.9355 | 0 | 0 | 48836.4922 | 0 | 0 | 0 | 0 | 2569.5715 | 110.3944 | 0 | 2459.1773 | 1359.8656 | 1102.1665 | -1129.6023 | 0.076423 | 0 | 1 | 1 | 1359.8656 | 175240.4121 | 1359.8656
EPr-w16-v14-VRF_HR_OAU1 | EPr | CZ16 | 14 | VRF_HR_OAU1 | 1.6302 | 395978.9375 | 133157.6562 | 0 | 99493.7734 | 102890.1719 | 11601.0547 | 0 | 0 | 48836.4961 | 0 | 0 | 0 | 0 | 2569.5715 | 110.3944 | 0 | 2459.1773 | 1267.4231 | 1102.1224 | -1129.5571 | 0.076423 | 0 | 1 | 1 | 1267.4231 | 163327.7227 | 1267.4231
EPr-w16-v14-VRF_HR_OAU2 | EPr | CZ16 | 14 | VRF_HR_OAU2 | 1.6302 | 385390.5938 | 133157.6562 | 0 | 99493.7734 | 93567.0938 | 10335.9785 | 0 | 0 | 48836.5039 | 0 | 0 | 0 | 0 | 2569.5715 | 110.3944 | 0 | 2459.1773 | 1185.2591 | 1102.0771 | -1129.5105 | 0.076423 | 0 | 1 | 1 | 1185.2591 | 152739.5762 | 1185.2591
Htl-w16-v14-FPFC_1 | Htl | CZ16 | 14 | FPFC_1 | 577.8195 | 3379882 | 566447.625 | 0 | 1692748 | 15168.2832 | 423255.6875 | 5614.3979 | 196980.7031 | 479666.0625 | 0 | 0 | 0 | 0 | 256089.7434 | 0 | 211497.5949 | 44592.1178 | 29802.7084 | 7197.166 | -14349.0566 | 0 | 0 | 0 | 0 | 29802.7084 | 1115070.7363 | 8652.9489
Htl-w16-v14-FPFC_2 | Htl | CZ16 | 14 | FPFC_2 | 534.4556 | 3277688.5 | 566447.625 | 0 | 1692748 | 27681.8633 | 299264.5312 | 9988.3174 | 196947.7656 | 484609.875 | 0 | 0 | 0 | 0 | 225215.9181 | 0 | 180623.5443 | 44592.3123 | 25888.3457 | 7197.166 | -14349.0566 | 0.7191 | 0 | 0 | 63 | 25888.3457 | 1008504.0352 | 7825.9913
Htl-w16-v14-VRF_HP_OAU0 | Htl | CZ16 | 14 | VRF_HP_OAU0 | 635.8603 | 4623747.5 | 566447.625 | 0 | 1692748 | 1597092.125 | 315321.6875 | 0 | 1121.6216 | 451016.875 | 0 | 0 | 0 | 0 | 44592.5478 | 0 | 0 | 44592.5478 | 18348.9259 | 7159.1602 | -7300.4683 | 0.10273 | 0 | 9 | 0 | 18348.9259 | 2364552.3091 | 18348.9259
Htl-w16-v14-VRF_HP_OAU1 | Htl | CZ16 | 14 | VRF_HP_OAU1 | 591.6698 | 4416527 | 566447.625 | 0 | 1692748 | 1435989.5 | 269202.8438 | 0 | 1121.6216 | 451016.6562 | 0 | 0 | 0 | 0 | 44592.5478 | 0 | 0 | 44592.5478 | 16740.8856 | 7159.125 | -7300.4307 | 0.10273 | 0 | 9 | 0 | 16740.8856 | 2157330.6216 | 16740.8856
Htl-w16-v14-VRF_HP_OAU2 | Htl | CZ16 | 14 | VRF_HP_OAU2 | 561.0098 | 4247984.5 | 566447.625 | 0 | 1692748 | 1301403.5 | 235245.3906 | 0 | 1121.6216 | 451016.5938 | 0 | 0 | 0 | 0 | 44592.5478 | 0 | 0 | 44592.5478 | 15432.9879 | 7159.0908 | -7300.395 | 0.10273 | 0 | 9 | 0 | 15432.9879 | 1988787.106 | 15432.9879
Htl-w16-v14-VRF_HR_OAU0 | Htl | CZ16 | 14 | VRF_HR_OAU0 | 617.594 | 4468652 | 566447.625 | 0 | 1692748 | 1442748.25 | 314833.0312 | 0 | 1121.6216 | 450751.8125 | 0 | 0 | 0 | 0 | 44592.5376 | 0 | 0 | 44592.5376 | 17145.3686 | 7092.5981 | -7231.8662 | 0.92455 | 0 | 77 | 4 | 17145.3686 | 2209454.7153 | 17145.3686
Htl-w16-v14-VRF_HR_OAU1 | Htl | CZ16 | 14 | VRF_HR_OAU1 | 579.6564 | 4275192.5 | 566447.625 | 0 | 1692748 | 1294341.75 | 269785.5 | 0 | 1121.6216 | 450747.1875 | 0 | 0 | 0 | 0 | 44592.5376 | 0 | 0 | 44592.5376 | 15644.1294 | 7092.498 | -7231.7598 | 0.92455 | 0 | 77 | 4 | 15644.1294 | 2015996.0591 | 15644.1294
Htl-w16-v14-VRF_HR_OAU2 | Htl | CZ16 | 14 | VRF_HR_OAU2 | 551.2182 | 4117854.5 | 566447.625 | 0 | 1692748 | 1170509.25 | 236281.8906 | 0 | 1121.6216 | 450744.125 | 0 | 0 | 0 | 0 | 44592.5376 | 0 | 0 | 44592.5376 | 14423.1774 | 7092.4087 | -7231.6636 | 0.93597 | 0 | 78 | 4 | 14423.1774 | 1858656.8872 | 14423.1774

## OfS_Svgs
|  |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 25 | 25 | 25 | 25 | 25 | 25 | [25 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [24 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | CoolCap | CoolCap | CoolCap | CoolCap | CoolCap | CoolCap |  |  | Baseline is One Speed T-24 AC/Furnace, |  |  |  | Baseline is One Speed T-24 AC/Furnace, | [5 empty] | Baseline is 2 Speed T-24 AC/Furnace, |  |  |  |  | Baseline is T-24 PVAV/Gas Boiler |  |  |  | Baseline is T-24 Heat Pump VRF System |  |  |  | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer |  | Baseline is One Speed T-24 AC/Furnace, | [9 empty] | Baseline is 2 Speed T-24 AC/Furnace, |  |  |  |  | Baseline is T-24 PVAV/Gas Boiler |  |  |  | Baseline is T-24 Heat Pump VRF System, |  |  |  | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating |  | Baseline is One Speed T-24 AC/Furnace, |  |  |  |  | Baseline is One Speed T-24 AC/Furnace, |  |  |  |  | Baseline is 2 Speed T-24 AC/Furnace, |  |  |  |  | Baseline is T-24 PVAV/Gas Boiler |  |  |  | Baseline is T24 Single-Mode VRF System,
|  | Sys ID | AC_S0Std | AC_S1Std | AC_SHi | AC_EStd | AC_EHi | PVAV_Std | PVAV_Hi | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 |  |  | < 65 kBtuh, with economizer |  |  |  | < 65 kBtuh, without economizer | [5 empty] | 65-135 kBtuh | [10 empty] | Baseline is T-24 Heat Recovery VRF System |  | AC_S0Std | AC_S1Std | AC_SHi | AC_EStd | AC_EHi | PVAV_Std | PVAV_Hi | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 |  | < 65 kBtuh, with economizer |  |  |  | < 65 kBtuh, no economizer | [5 empty] | 65-135 kBtuh | [8 empty] | 14 | tons/system |  |  | AC_S0Std | AC_S1Std | AC_SHi | AC_EStd | AC_EHi | PVAV_Std | PVAV_Hi | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 |  | < 65 kBtuh |  |  |  |  | < 65 kBtuh, no economizer |  |  |  |  | 65-135 kBtuh
Bldg | CZ | [20 empty] | CZ | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff PVAV | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP Tier1 | VRF HP Tier2 | VRF HR Tier1 | VRF HR Tier2 | [7 empty] | HP0 | HP1 | HP2 | HR0 | HR1 | HR2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff PVAV | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP Tier1 | VRF HP Tier2 | VRF HP Tier3 | VRF HP Tier4 | [13 empty] | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff PVAV | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP Tier1 | VRF HP Tier2 | VRF HR Tier1 | VRF HR Tier2
OfS | 1 |  | 91749.1406 | 89107.625 | 85802.7422 | 87499.7969 | 87430.1094 | 88251.7031 | 87877.2891 | 93941.7656 | 93202.3438 | 92566.7969 | 93061.2188 | 92404.4141 | 91818.6797 | 16.0248 | 16.0248 | 16.0248 | 16.0248 | 16.0248 | 16.0248 | CZ01 | 206.2353 | -301.6659 | -255.5236 | -246.7169 | -169.1785 | 371.0743 | -136.8268 | -51.0244 | -81.8779 | -4.3395 | 4.3487 | -401.9995 | -355.8572 | -347.0506 | -269.5121 | 23.3646 | -355.0782 | -269.2757 | -300.1292 | -222.5908 | 46.1423 | 85.8025 | 40.9867 | 77.5384 | 27.0094 | 25.3837 | 24.0266 | 25.7229 | 25.1266 | 28.7278 | 27.2078 | 26.164 | 25.6628 | 25.1979 | 26.0643 | 25.6007 | 25.202 | 0.084688 | -0.048688 | 0.011596 | -0.042472 | 0.011344 | 0.18614 | 0.052761 | 0.11304 | 0.058976 | 0.11279 | 0.037208 | -0.027524 | 0.032759 | -0.021308 | 0.032508 | 0.094855 | 0.15999 | 0.22028 | 0.16621 | 0.22002 | 0.031277 | 0.060283 | 0.028931 | 0.053816 | 517.2755 | 517.6463 | 576.5512 | 552.734 | 552.734 | 615.1502 | 439.4049 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6759 | 32.3028 | 32.3028 | 32.3028 | 32.3028 | -3.699 | 32.2797 | 32.2797 | 32.2797 | 32.2797 | 0 | 34.4924 | 34.4924 | 34.4924 | 34.4924 | 10.9671 | 38.3873 | 38.3873 | 38.3873 | 38.3873 | 0 | 0 | 0 | 0
OfS | 2 |  | 102745.1797 | 99246.1094 | 93188.2891 | 97817.625 | 96319.7812 | 99318.9062 | 96312.5781 | 100233.4766 | 98737.8359 | 97465.6406 | 99037.8281 | 97696.4766 | 96548.0938 | 20.74 | 20.74 | 20.74 | 20.74 | 20.74 | 20.74 | CZ02 | 292.0843 | -47.607 | 24.507 | 10.0425 | 130.0877 | 460.7958 | 121.1045 | 254.5587 | 178.7539 | 298.7992 | 72.2201 | -116.4829 | -44.369 | -58.8334 | 61.2118 | 144.9533 | -44.097 | 89.3572 | 13.5525 | 133.5977 | 72.1139 | 133.4542 | 64.6747 | 120.0452 | 39.1729 | 39.1715 | 35.2189 | 40.7419 | 37.6873 | 43.1525 | 38.1535 | 38.5875 | 36.5264 | 34.8006 | 38.2281 | 36.085 | 34.3452 | 0.19058 | 0.028161 | 0.21075 | 0.04549 | 0.23271 | 0.19065 | 0.028228 | 0.21081 | 0.045556 | 0.23277 | 0.14728 | 0.10388 | 0.28646 | 0.12121 | 0.30842 | 0.24103 | 0.22011 | 0.40269 | 0.23744 | 0.42465 | 0.099375 | 0.18259 | 0.10333 | 0.18722 | 236.321 | 236.5244 | 266.5959 | 248.3891 | 248.3891 | 339.3421 | 234.492 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4499 | 11.4043 | 11.4043 | 11.4043 | 11.4043 | -1.4597 | 11.3945 | 11.3945 | 11.3945 | 11.3945 | 0 | 11.9763 | 11.9763 | 11.9763 | 11.9763 | 5.0555 | 16.3617 | 16.3617 | 16.3617 | 16.3617 | 0 | 0 | 0 | 0
OfS | 3 |  | 98011.1016 | 93942.0703 | 89553.7969 | 92920.6875 | 92162.7109 | 94478.0625 | 92586.9844 | 96118.1172 | 95048.7266 | 94147.6797 | 95255.75 | 94306.2656 | 93503.3828 | 18.9437 | 18.9437 | 18.9437 | 18.9437 | 18.9437 | 18.9437 | CZ03 | 231.6487 | -114.8694 | -58.4183 | -69.3467 | 23.1575 | 446.4453 | 99.9271 | 203.9428 | 145.4499 | 237.954 | 40.0122 | -168.7863 | -112.3352 | -123.2636 | -30.7594 | 99.8265 | -86.5754 | 17.4403 | -41.0527 | 51.4515 | 56.4511 | 104.0157 | 50.1215 | 92.5042 | 32.3545 | 32.3553 | 29.671 | 33.3169 | 31.4432 | 35.6252 | 32.4617 | 31.2316 | 30.1333 | 29.1765 | 30.7528 | 29.7434 | 28.8972 | 0.1417 | 0.059321 | 0.1678 | 0.084596 | 0.18255 | 0.14166 | 0.059279 | 0.16776 | 0.084553 | 0.18251 | 0.098908 | 0.11008 | 0.21856 | 0.13536 | 0.23331 | 0.167 | 0.23193 | 0.34042 | 0.25721 | 0.35516 | 0.057976 | 0.10848 | 0.053286 | 0.097952 | 163.2842 | 163.4544 | 190.2383 | 176.8689 | 176.8689 | 245.7036 | 164.5615 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4139 | 8.6285 | 8.6285 | 8.6285 | 8.6285 | -1.4229 | 8.6195 | 8.6195 | 8.6195 | 8.6195 | 0 | 9.3366 | 9.3366 | 9.3366 | 9.3366 | 4.2833 | 12.9702 | 12.9702 | 12.9702 | 12.9702 | 0 | 0 | 0 | 0
OfS | 4 |  | 103473.2188 | 99678.2969 | 93969.2188 | 99004.7656 | 97313.0547 | 101352.1328 | 97880.5078 | 100640.4141 | 99057.7188 | 97719.0234 | 99637.6719 | 98161.7109 | 96923.1719 | 20.0474 | 20.0474 | 20.0474 | 20.0474 | 20.0474 | 20.0474 | CZ04 | 284.7792 | -47.9922 | 30.9556 | 2.0264 | 137.4306 | 474.0768 | 141.3054 | 287.0297 | 191.324 | 326.7282 | 84.3856 | -81.5891 | -2.6414 | -31.5705 | 103.8337 | 173.171 | 35.5018 | 181.2261 | 85.5204 | 220.9246 | 78.9477 | 145.7243 | 73.6236 | 135.4042 | 37.3598 | 37.3553 | 34.098 | 39.1584 | 36.3825 | 41.8603 | 37.2385 | 37.1539 | 35.3165 | 33.7657 | 36.5883 | 34.7484 | 33.236 | 0.16248 | 0.010047 | 0.17905 | 0.038258 | 0.20548 | 0.1627 | 0.010271 | 0.17928 | 0.038482 | 0.2057 | 0.13846 | 0.099988 | 0.26899 | 0.1282 | 0.29542 | 0.23054 | 0.23477 | 0.40377 | 0.26298 | 0.4302 | 0.091649 | 0.16901 | 0.091776 | 0.16722 | 122.957 | 123.1209 | 142.5916 | 131.8623 | 131.8623 | 214.5718 | 140.0755 | 0 | 0 | 0 | 0 | 0 | 0 | -0.97123 | 6.1415 | 6.1415 | 6.1415 | 6.1415 | -0.97941 | 6.1333 | 6.1333 | 6.1333 | 6.1333 | 0 | 6.5775 | 6.5775 | 6.5775 | 6.5775 | 3.716 | 10.7032 | 10.7032 | 10.7032 | 10.7032 | 0 | 0 | 0 | 0
OfS | 5 |  | 97156.7266 | 93462.5547 | 89291.0703 | 92517.1797 | 91749.2578 | 95055.3281 | 93145.0703 | 95856.4766 | 94812.7031 | 93926.5312 | 94961.6406 | 94042.0703 | 93237.6172 | 17.5052 | 17.5052 | 17.5052 | 17.5052 | 17.5052 | 17.5052 | CZ05 | 238.2992 | -136.7546 | -77.1283 | -85.6364 | 12.8497 | 449.3317 | 74.2778 | 184.5274 | 125.396 | 223.8821 | 43.8681 | -190.7599 | -131.1335 | -139.6417 | -41.1555 | 109.1249 | -45.7662 | 64.4834 | 5.352 | 103.8381 | 59.6264 | 110.2496 | 52.5312 | 98.4862 | 30.2608 | 30.1289 | 27.7745 | 30.7889 | 29.3213 | 32.9901 | 30.5436 | 29.3567 | 28.4383 | 27.7014 | 28.8604 | 27.7478 | 27.0882 | 0.1345 | 0.044115 | 0.13867 | 0.072466 | 0.1737 | 0.14204 | 0.051651 | 0.14621 | 0.080002 | 0.18124 | 0.083841 | 0.08182 | 0.17638 | 0.11017 | 0.21141 | 0.13976 | 0.20756 | 0.30212 | 0.23591 | 0.33715 | 0.052461 | 0.094559 | 0.063554 | 0.10124 | 169.1816 | 169.4187 | 192.9902 | 182.2138 | 182.2138 | 272.2216 | 181.8926 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3465 | 9.6782 | 9.6782 | 9.6782 | 9.6782 | -1.3601 | 9.6646 | 9.6646 | 9.6646 | 9.6646 | 0 | 10.4091 | 10.4091 | 10.4091 | 10.4091 | 5.1601 | 15.5509 | 15.5509 | 15.5509 | 15.5509 | 0 | 0 | 0 | 0
OfS | 6 |  | 105074.5703 | 101299.7031 | 95366.9922 | 100973.6406 | 98956.2656 | 104350.2344 | 100214.3906 | 101261.9297 | 99600.9219 | 98198.5547 | 99933.7812 | 98409.8594 | 97126.1016 | 22.0608 | 22.0608 | 22.0608 | 22.0608 | 22.0608 | 22.0608 | CZ06 | 268.926 | 1.7122 | 77.0047 | 61.9164 | 189.1867 | 440.0383 | 172.8246 | 311.6854 | 233.0287 | 360.299 | 91.4463 | -13.068 | 62.2245 | 47.1362 | 174.4065 | 187.4752 | 139.9909 | 278.8517 | 200.195 | 327.4653 | 75.2924 | 138.8608 | 69.0784 | 127.2703 | 35.2581 | 35.258 | 32.3828 | 37.0013 | 34.5889 | 39.39 | 35.4785 | 34.9187 | 33.3196 | 31.9898 | 34.8647 | 33.3256 | 32.0302 | 0.13033 | 0.015383 | 0.14815 | 0.01783 | 0.14632 | 0.13034 | 0.015384 | 0.14815 | 0.017831 | 0.14632 | 0.10935 | 0.094403 | 0.22717 | 0.096849 | 0.22533 | 0.1773 | 0.20268 | 0.33545 | 0.20513 | 0.33361 | 0.072483 | 0.13277 | 0.069767 | 0.12849 | 44.3012 | 44.3835 | 53.76 | 48.8478 | 48.8478 | 116.8145 | 72.9107 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42503 | 2.0119 | 2.0119 | 2.0119 | 2.0119 | -0.42876 | 2.0081 | 2.0081 | 2.0081 | 2.0081 | 0 | 2.2142 | 2.2142 | 2.2142 | 2.2142 | 1.9901 | 5.2951 | 5.2951 | 5.2951 | 5.2951 | 0 | 0 | 0 | 0
OfS | 7 |  | 104310.1875 | 99218.0078 | 94028.9844 | 99184.4219 | 97502.1562 | 102835.6953 | 99048.5703 | 100426.6172 | 98834.1172 | 97499.5938 | 99354.125 | 97884.1484 | 96649.2734 | 21.5939 | 21.5939 | 21.5939 | 21.5939 | 21.5939 | 21.5939 | CZ07 | 240.3008 | -55.97 | 17.7778 | -6.3035 | 118.9567 | 476.1168 | 179.846 | 315.3948 | 229.5125 | 354.7727 | 77.9048 | -57.5254 | 16.2224 | -7.8589 | 117.4013 | 175.3797 | 111.5631 | 247.1119 | 161.2296 | 286.4898 | 73.7478 | 135.5488 | 68.0738 | 125.2602 | 33.3826 | 33.3826 | 30.8524 | 35.0125 | 32.9086 | 37.2875 | 33.7936 | 32.9332 | 31.6171 | 30.5096 | 32.6948 | 31.41 | 30.3282 | 0.11717 | 0.020813 | 0.13305 | 0.031851 | 0.14145 | 0.11717 | 0.020813 | 0.13305 | 0.031851 | 0.14145 | 0.09743 | 0.096292 | 0.20853 | 0.10733 | 0.21693 | 0.1618 | 0.20165 | 0.31388 | 0.21268 | 0.32228 | 0.060945 | 0.11224 | 0.059501 | 0.1096 | 10.6844 | 10.7258 | 14.2238 | 12.2623 | 12.2623 | 43.2694 | 23.9969 | 0 | 0 | 0 | 0 | 0 | 0 | -0.16199 | 0.49671 | 0.49671 | 0.49671 | 0.49671 | -0.16391 | 0.49479 | 0.49479 | 0.49479 | 0.49479 | 0 | 0.56786 | 0.56786 | 0.56786 | 0.56786 | 0.8925 | 2.0038 | 2.0038 | 2.0038 | 2.0038 | 0 | 0 | 0 | 0
OfS | 8 |  | 108797.2656 | 104673.5938 | 97604.1172 | 104113.8516 | 101662.6406 | 107462.2266 | 102546.1953 | 104053.8906 | 102060.4922 | 100389.4844 | 102654.3828 | 100827.8672 | 99288.4844 | 23.5204 | 23.5204 | 23.5204 | 23.5204 | 23.5204 | 23.5204 | CZ08 | 300.5678 | 26.3475 | 111.0993 | 85.8493 | 228.9548 | 475.8909 | 201.6706 | 357.4675 | 261.1725 | 404.2779 | 104.2163 | 2.5493 | 87.3012 | 62.0512 | 205.1566 | 209.0113 | 144.9097 | 300.7066 | 204.4116 | 347.517 | 84.7519 | 155.7969 | 77.6566 | 143.1054 | 38.3444 | 38.3445 | 34.5067 | 39.8953 | 37.0055 | 42.4755 | 37.6817 | 37.5952 | 35.7216 | 34.1484 | 37.0789 | 35.2705 | 33.7517 | 0.16317 | 0.031857 | 0.1784 | 0.053808 | 0.19527 | 0.16317 | 0.031856 | 0.1784 | 0.053807 | 0.19527 | 0.12286 | 0.097791 | 0.24434 | 0.11974 | 0.2612 | 0.20381 | 0.20749 | 0.35404 | 0.22944 | 0.3709 | 0.079659 | 0.14655 | 0.076883 | 0.14146 | 34.9579 | 35.0054 | 43.1555 | 38.6743 | 38.6743 | 89.168 | 57.4769 | 0 | 0 | 0 | 0 | 0 | 0 | -0.34651 | 1.4883 | 1.4883 | 1.4883 | 1.4883 | -0.34853 | 1.4863 | 1.4863 | 1.4863 | 1.4863 | 0 | 1.6443 | 1.6443 | 1.6443 | 1.6443 | 1.3474 | 3.7911 | 3.7911 | 3.7911 | 3.7911 | 0 | 0 | 0 | 0
OfS | 9 |  | 112137.4609 | 107522.5312 | 99124.3203 | 106164.3438 | 103493.6797 | 108377.4922 | 103550.9609 | 105939.9219 | 103775.375 | 101951.7578 | 104451 | 102460.6719 | 100786.3203 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | 26.706 | CZ09 | 314.4685 | 59.2603 | 140.3112 | 115.0126 | 252.2354 | 487.2732 | 232.065 | 381.4007 | 287.8173 | 425.0401 | 100.0022 | 8.4034 | 89.4542 | 64.1557 | 201.3785 | 180.728 | 91.2741 | 240.6097 | 147.0263 | 284.2492 | 81.0508 | 149.3356 | 74.5273 | 137.2229 | 43.918 | 43.918 | 38.8186 | 45.8512 | 42.0052 | 48.7904 | 42.4158 | 43.5573 | 40.9736 | 38.8057 | 42.86 | 40.3656 | 38.2728 | 0.19094 | 0.013506 | 0.19143 | 0.039618 | 0.21138 | 0.19094 | 0.013506 | 0.19143 | 0.039618 | 0.21138 | 0.14401 | 0.085895 | 0.26382 | 0.11201 | 0.28377 | 0.2387 | 0.19595 | 0.37387 | 0.22206 | 0.39383 | 0.096745 | 0.17792 | 0.093399 | 0.17176 | 36.6319 | 36.6984 | 47.1556 | 40.5995 | 40.5995 | 86.8175 | 55.6324 | 0 | 0 | 0 | 0 | 0 | 0 | -0.39157 | 1.3742 | 1.3742 | 1.3742 | 1.3742 | -0.39406 | 1.3717 | 1.3717 | 1.3717 | 1.3717 | 0 | 1.5202 | 1.5202 | 1.5202 | 1.5202 | 1.1677 | 3.2509 | 3.2509 | 3.2509 | 3.2509 | 0 | 0 | 0 | 0
OfS | 10 |  | 112252.625 | 108107.6094 | 100002.0938 | 107278.9219 | 104340.9219 | 110258.125 | 104816.4062 | 106994.4062 | 104666.875 | 102705.25 | 105516.7188 | 103355.7266 | 101539.4219 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | 24.1726 | CZ10 | 335.3186 | 46.0523 | 142.3404 | 107.183 | 271.7206 | 506.7945 | 217.5282 | 394.9672 | 278.659 | 443.1965 | 121.5427 | 11.7702 | 108.0583 | 72.9009 | 237.4385 | 225.1195 | 135.0174 | 312.4563 | 196.1481 | 360.6857 | 96.2881 | 177.4389 | 89.3985 | 164.5375 | 44.6956 | 44.6954 | 40 | 47.0328 | 42.9885 | 49.6661 | 43.1052 | 45.5965 | 42.7461 | 40.3598 | 44.9341 | 42.1703 | 39.8555 | 0.19425 | -0.037276 | 0.17936 | -0.0098728 | 0.20023 | 0.19425 | -0.037268 | 0.17937 | -0.0098649 | 0.20023 | 0.16731 | 0.05942 | 0.27606 | 0.086823 | 0.29692 | 0.27142 | 0.16836 | 0.385 | 0.19576 | 0.40586 | 0.11792 | 0.21664 | 0.11434 | 0.2101 | 48.0145 | 48.0881 | 58.6105 | 52.1872 | 52.1872 | 103.9317 | 66.0764 | 0 | 0 | 0 | 0 | 0 | 0 | -0.4353 | 1.9894 | 1.9894 | 1.9894 | 1.9894 | -0.43835 | 1.9863 | 1.9863 | 1.9863 | 1.9863 | 0 | 2.1589 | 2.1589 | 2.1589 | 2.1589 | 1.566 | 4.2996 | 4.2996 | 4.2996 | 4.2996 | 0 | 0 | 0 | 0
OfS | 11 |  | 112625.7266 | 109339.0859 | 100674.0547 | 108176.7188 | 105158.5781 | 109924.5234 | 104619.1875 | 108806.875 | 106331.9531 | 104232.9297 | 107319.6562 | 104995.5781 | 103029.3906 | 24.3273 | 24.3273 | 24.3273 | 24.3273 | 24.3273 | 24.3273 | CZ11 | 356.1855 | 21.8771 | 123.6115 | 83.0109 | 259.3669 | 491.2865 | 156.9781 | 344.9951 | 218.1118 | 394.4678 | 124.064 | -25.9033 | 75.8311 | 35.2305 | 211.5865 | 218.0816 | 45.9422 | 233.9592 | 107.0759 | 283.4319 | 101.7344 | 188.017 | 95.5338 | 176.356 | 44.5271 | 44.5263 | 39.5183 | 46.439 | 42.4738 | 47.931 | 41.8133 | 43.952 | 41.303 | 39.035 | 43.2172 | 40.6611 | 38.5192 | 0.20586 | 0.023609 | 0.22573 | 0.053812 | 0.24693 | 0.20589 | 0.023643 | 0.22576 | 0.053846 | 0.24696 | 0.163 | 0.10223 | 0.30435 | 0.13244 | 0.32555 | 0.25148 | 0.16356 | 0.36568 | 0.19377 | 0.38688 | 0.10889 | 0.20212 | 0.10507 | 0.19312 | 261.3865 | 261.5185 | 299.9369 | 278.5824 | 278.5824 | 343.7807 | 246.5051 | 0 | 0 | 0 | 0 | 0 | 0 | -1.5792 | 10.75 | 10.75 | 10.75 | 10.75 | -1.5847 | 10.7446 | 10.7446 | 10.7446 | 10.7446 | 0 | 11.4514 | 11.4514 | 11.4514 | 11.4514 | 3.9986 | 14.1315 | 14.1315 | 14.1315 | 14.1315 | 0 | 0 | 0 | 0
OfS | 12 |  | 108719.0391 | 105020.3438 | 97285.6094 | 103503.375 | 101240.0938 | 104767.3281 | 100638.9688 | 104677.6797 | 102660.3047 | 100969.1797 | 103269.1875 | 101410.6016 | 99837.25 | 23.9264 | 23.9264 | 23.9264 | 23.9264 | 23.9264 | 23.9264 | CZ12 | 323.2725 | 14.3216 | 98.6376 | 73.1894 | 216.6269 | 477.8591 | 168.9082 | 323.9046 | 227.776 | 371.2135 | 94.5936 | -49.0799 | 35.236 | 9.7878 | 153.2253 | 172.5444 | 3.7468 | 158.7432 | 62.6146 | 206.0521 | 84.316 | 154.9964 | 77.6794 | 143.4375 | 42.0349 | 42.0348 | 36.9472 | 43.3264 | 39.8521 | 45.8279 | 40.1267 | 40.7297 | 38.4707 | 36.576 | 39.8811 | 37.7276 | 35.9206 | 0.21264 | 0.054549 | 0.22815 | 0.090015 | 0.25554 | 0.21264 | 0.05455 | 0.22815 | 0.090016 | 0.25554 | 0.14521 | 0.10853 | 0.28213 | 0.144 | 0.30952 | 0.23828 | 0.21308 | 0.38668 | 0.24855 | 0.41407 | 0.094414 | 0.1736 | 0.090007 | 0.16553 | 239.6621 | 239.8006 | 273.1003 | 251.1273 | 251.1273 | 321.0982 | 228.7223 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3918 | 10.0224 | 10.0224 | 10.0224 | 10.0224 | -1.3975 | 10.0167 | 10.0167 | 10.0167 | 10.0167 | 0 | 10.4958 | 10.4958 | 10.4958 | 10.4958 | 3.8608 | 13.4203 | 13.4203 | 13.4203 | 13.4203 | 0 | 0 | 0 | 0
OfS | 13 |  | 113101.5234 | 109891.6641 | 101299.7188 | 109142.5078 | 105972.7031 | 110938.7812 | 105446.1562 | 109466.25 | 106920.3125 | 104766.5781 | 107779.6406 | 105410.9844 | 103411.8516 | 25.7521 | 25.7521 | 25.7521 | 25.7521 | 25.7521 | 25.7521 | CZ13 | 333.6411 | 16.5196 | 115.3831 | 82.0138 | 251.623 | 458.2858 | 141.1644 | 323.6613 | 206.6585 | 376.2678 | 123.0894 | -12.5715 | 86.2919 | 52.9226 | 222.5319 | 213.2887 | 57.1811 | 239.678 | 122.6752 | 292.2845 | 98.8634 | 182.4969 | 91.9793 | 169.6093 | 42.6845 | 42.6842 | 37.8261 | 44.3831 | 40.7712 | 46.953 | 41.015 | 42.278 | 39.8396 | 37.796 | 41.4402 | 39.1081 | 37.1518 | 0.18865 | 0.015775 | 0.18982 | 0.048307 | 0.21483 | 0.18866 | 0.015787 | 0.18983 | 0.048319 | 0.21485 | 0.14025 | 0.081743 | 0.25579 | 0.11428 | 0.2808 | 0.23058 | 0.18154 | 0.35558 | 0.21407 | 0.3806 | 0.094689 | 0.17405 | 0.090561 | 0.16653 | 232.4603 | 232.5685 | 267.9292 | 247.4643 | 247.4643 | 291.6362 | 211.7295 | 0 | 0 | 0 | 0 | 0 | 0 | -1.3731 | 9.0311 | 9.0311 | 9.0311 | 9.0311 | -1.3773 | 9.0269 | 9.0269 | 9.0269 | 9.0269 | 0 | 9.6095 | 9.6095 | 9.6095 | 9.6095 | 3.1029 | 11.3248 | 11.3248 | 11.3248 | 11.3248 | 0 | 0 | 0 | 0
OfS | 14 |  | 113138.4688 | 110081.8047 | 101384.3281 | 109194.7422 | 105938.3047 | 111291.1484 | 105697.7266 | 109859.5859 | 107254.9062 | 105067.1953 | 108056.9141 | 105644.8281 | 103595.7266 | 24.8957 | 24.8957 | 24.8957 | 24.8957 | 24.8957 | 24.8957 | CZ14 | 349.356 | 8.926 | 113.5495 | 81.3348 | 260.5296 | 472.1346 | 131.7046 | 324.203 | 204.1134 | 383.3082 | 130.803 | -26.7051 | 77.9184 | 45.7037 | 224.8985 | 224.6738 | 57.5023 | 250.0007 | 129.9111 | 309.1059 | 104.6235 | 192.4984 | 96.8875 | 179.1948 | 43.6732 | 43.6725 | 39.0334 | 45.5089 | 41.691 | 47.7562 | 41.6811 | 42.9855 | 40.3789 | 38.227 | 42.5486 | 40.0808 | 37.8262 | 0.18634 | 0.027598 | 0.21873 | 0.045148 | 0.23483 | 0.18637 | 0.027625 | 0.21876 | 0.045175 | 0.23486 | 0.15336 | 0.10136 | 0.2925 | 0.11891 | 0.3086 | 0.24402 | 0.19163 | 0.38276 | 0.20918 | 0.39886 | 0.1047 | 0.19114 | 0.099124 | 0.18969 | 249.9821 | 250.1853 | 277.2329 | 258.6699 | 258.6699 | 321.9241 | 225.3898 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0864 | 10.0493 | 10.0493 | 10.0493 | 10.0493 | -1.0946 | 10.0412 | 10.0412 | 10.0412 | 10.0412 | 0 | 10.3901 | 10.3901 | 10.3901 | 10.3901 | 3.8775 | 12.9309 | 12.9309 | 12.9309 | 12.9309 | 0 | 0 | 0 | 0
OfS | 15 |  | 135503.5312 | 131345.1719 | 116390.2969 | 130253.7188 | 123895.5312 | 134846.8594 | 124254.9688 | 125929.4453 | 121444.0391 | 117675.9844 | 123111.0078 | 118965.2812 | 115476.3438 | 31.2968 | 31.2968 | 31.2968 | 31.2968 | 31.2968 | 31.2968 | CZ15 | 477.8411 | 173.0444 | 316.363 | 263.0996 | 507.044 | 610.7099 | 305.9131 | 569.6293 | 395.9684 | 639.9127 | 203.1581 | 138.17 | 281.4886 | 228.2253 | 472.1696 | 338.4342 | 284.931 | 548.6472 | 374.9863 | 618.9306 | 143.3186 | 263.7162 | 132.4651 | 243.9443 | 51.5032 | 51.5033 | 44.1395 | 52.9861 | 47.9626 | 54.4044 | 46.7868 | 48.7577 | 45.5557 | 42.8732 | 47.0856 | 44.0965 | 41.5906 | 0.23529 | 0.087729 | 0.27575 | 0.14116 | 0.31673 | 0.23529 | 0.087728 | 0.27575 | 0.14115 | 0.31673 | 0.16051 | 0.13511 | 0.32313 | 0.18854 | 0.36411 | 0.2434 | 0.18043 | 0.36845 | 0.23385 | 0.40943 | 0.10231 | 0.18802 | 0.095506 | 0.17558 | 6.8393 | 6.863 | 9.4278 | 7.4214 | 7.4214 | 31.0098 | 18.0164 | 0 | 0 | 0 | 0 | 0 | 0 | -0.081951 | 0.21929 | 0.21929 | 0.21929 | 0.21929 | -0.082706 | 0.21853 | 0.21853 | 0.21853 | 0.21853 | 0 | 0.23713 | 0.23713 | 0.23713 | 0.23713 | 0.41517 | 0.99083 | 0.99083 | 0.99083 | 0.99083 | 0 | 0 | 0 | 0
OfS | 16 |  | 98746.3203 | 96256.7969 | 91249.0547 | 95439.2188 | 94297.8359 | 95893.1016 | 93926.4844 | 104723.25 | 102938.5156 | 101389.5391 | 102819.6172 | 101204.3125 | 99799.1484 | 20.432 | 20.432 | 20.432 | 20.432 | 20.432 | 20.432 | CZ16 | 245.0927 | -414.3716 | -327.0218 | -321.2025 | -173.3725 | 366.9369 | -292.5274 | -129.3664 | -199.3584 | -51.5283 | 55.8624 | -454.3861 | -367.0363 | -361.2171 | -213.387 | 96.2517 | -432.1718 | -269.0108 | -339.0028 | -191.1727 | 87.3498 | 163.161 | 79.0575 | 147.8301 | 33.2316 | 33.2295 | 30.2233 | 34.1681 | 32.1691 | 36.356 | 33.1724 | 32.096 | 30.9271 | 29.8839 | 31.7224 | 30.5281 | 29.3925 | 0.14714 | 0.055479 | 0.16374 | 0.073762 | 0.18779 | 0.14724 | 0.055581 | 0.16385 | 0.073864 | 0.1879 | 0.097835 | 0.10141 | 0.20968 | 0.1197 | 0.23373 | 0.15582 | 0.2085 | 0.31676 | 0.22678 | 0.34081 | 0.057209 | 0.10827 | 0.058454 | 0.11403 | 1077.7452 | 1078.1222 | 1152.0232 | 1118.7658 | 1118.7658 | 1090.8894 | 850.2291 | 0 | 0 | 0 | 0 | 0 | 0 | -3.6169 | 52.7663 | 52.7663 | 52.7663 | 52.7663 | -3.6354 | 52.7478 | 52.7478 | 52.7478 | 52.7478 | 0 | 54.7555 | 54.7555 | 54.7555 | 54.7555 | 11.7786 | 53.3911 | 53.3911 | 53.3911 | 53.3911 | 0 | 0 | 0 | 0
|  |  | Baseline is One Speed T-24 AC/Furnace, < 65 kBtuh, with economizer | [8 empty] | Baseline is One Speed T-24 AC/Furnace, < 65 kBtuh, without economizer | [10 empty] | Baseline is 2 Speed T-24 AC/Furnace, 65-135 kBtuh | [7 empty] | Baseline is T-24 PVAV/Gas Boiler | [7 empty] | Baseline is T-24 Heat Pump VRF System | [9 empty] | Baseline is T-24 Heat Recovery VRF System
-454.3861
639.9127
-0.048688
0.4302
-3.699
54.7555

## EPr_Svgs
|  |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 25 | 25 | 25 | 25 | 25 | 25 | [25 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [24 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | CoolCap | CoolCap | CoolCap | CoolCap | CoolCap | CoolCap |  |  | Baseline is One Speed T-24 AC/Furnace, |  |  |  | Baseline is One Speed T-24 AC/Furnace, | [5 empty] | Baseline is 2 Speed T-24 AC/Furnace, |  |  |  |  | Baseline is T-24 PVAV/Gas Boiler |  |  |  | Baseline is T-24 Heat Pump VRF System |  |  |  | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer |  | Baseline is One Speed T-24 AC/Furnace, | [9 empty] | Baseline is 2 Speed T-24 AC/Furnace, |  |  |  |  | Baseline is T-24 PVAV/Gas Boiler |  |  |  | Baseline is T-24 Heat Pump VRF System, |  |  |  | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating |  | Baseline is One Speed T-24 AC/Furnace, |  |  |  |  | Baseline is One Speed T-24 AC/Furnace, |  |  |  |  | Baseline is 2 Speed T-24 AC/Furnace, |  |  |  |  | Baseline is T-24 PVAV/Gas Boiler |  |  |  | Baseline is T24 Single-Mode VRF System,
|  | Sys ID | AC_S0Std | AC_S1Std | AC_SHi | AC_EStd | AC_EHi | PVAV_Std | PVAV_Hi | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 |  |  | < 65 kBtuh, with economizer |  |  |  | < 65 kBtuh, without economizer | [5 empty] | 65-135 kBtuh | [10 empty] | Baseline is T-24 Heat Recovery VRF System |  | AC_S0Std | AC_S1Std | AC_SHi | AC_EStd | AC_EHi | PVAV_Std | PVAV_Hi | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 |  | < 65 kBtuh, with economizer |  |  |  | < 65 kBtuh, no economizer | [5 empty] | 65-135 kBtuh | [8 empty] | 14 | tons/system |  |  | AC_S0Std | AC_S1Std | AC_SHi | AC_EStd | AC_EHi | PVAV_Std | PVAV_Hi | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 |  | < 65 kBtuh |  |  |  |  | < 65 kBtuh, no economizer |  |  |  |  | 65-135 kBtuh
Bldg | CZ | [20 empty] | CZ | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff PVAV | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP Tier1 | VRF HP Tier2 | VRF HR Tier1 | VRF HR Tier2 | [7 empty] | HP0 | HP1 | HP2 | HR0 | HR1 | HR2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff PVAV | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP Tier1 | VRF HP Tier2 | VRF HP Tier3 | VRF HP Tier4 | [13 empty] | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff AC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | Hi Eff PVAV | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP Tier1 | VRF HP Tier2 | VRF HR Tier1 | VRF HR Tier2
EPr | 1 |  | 277689.0625 | 277371.4062 | 266385.9375 | 275669 | 275336.8438 | 287817.4375 | 285650.4688 | 365247.5625 | 357245.125 | 350175.6562 | 353799.1562 | 346651.3438 | 340454.9688 | 77.4037 | 77.4037 | 77.4037 | 77.4037 | 77.4037 | 77.4037 | CZ01 | 141.9244 | -1135.2971 | -1031.9113 | -987.3919 | -814.9945 | 146.0283 | -1131.1932 | -936.4749 | -983.288 | -810.8906 | 4.2912 | -1157.291 | -1053.9052 | -1009.3857 | -836.9884 | 27.9957 | -1000.3418 | -805.6236 | -852.4366 | -680.0393 | 103.3858 | 194.7182 | 92.3446 | 172.3974 | 101.5844 | 101.0438 | 94.7948 | 102.9483 | 100.4078 | 112.202 | 106.2448 | 107.1133 | 104.9332 | 103.3597 | 105.1705 | 103.5775 | 102.1859 | 0.080733 | -0.078414 | -0.029919 | -0.053314 | -0.014754 | 0.087716 | -0.07143 | -0.022936 | -0.046331 | -0.0077712 | 0.032822 | -0.053809 | -0.0053144 | -0.028709 | 0.0098504 | 0.076963 | 0.065742 | 0.11424 | 0.090841 | 0.1294 | 0.028165 | 0.048494 | 0.020581 | 0.03856 | 14282.5587 | 14282.5805 | 14649.2339 | 14309.4426 | 14309.4426 | 14218.8698 | 13261.1635 | 0 | 0 | 0 | 0 | 0 | 0 | -4.7369 | 184.5207 | 184.5207 | 184.5207 | 184.5207 | -4.7372 | 184.5204 | 184.5204 | 184.5204 | 184.5204 | 0 | 184.8678 | 184.8678 | 184.8678 | 184.8678 | 12.3729 | 183.6976 | 183.6976 | 183.6976 | 183.6976 | 0 | 0 | 0 | 0
EPr | 2 |  | 321547.375 | 317011.0938 | 294714.2812 | 317344.1875 | 312013.9375 | 314608.6562 | 304967.3438 | 368148.75 | 359583.2188 | 352132.6562 | 357226.875 | 349664.8438 | 343008.3125 | 116.7182 | 116.7182 | 116.7182 | 116.7182 | 116.7182 | 116.7182 | CZ02 | 191.0311 | -438.1291 | -364.7427 | -344.5544 | -222.7349 | 229.8963 | -399.2639 | -262.0437 | -305.6892 | -183.8696 | 45.6677 | -435.2753 | -361.8889 | -341.7006 | -219.881 | 82.6033 | -458.7123 | -321.4922 | -365.1376 | -243.3181 | 73.3864 | 137.2202 | 64.7888 | 121.8196 | 1.7038 | 1.7037 | 1.6875 | 1.7177 | 1.7042 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 0.00013906 | 0.00062976 | 0.00062976 | 0.00062976 | 0.00062976 | 0.00013941 | 0.00063011 | 0.00063011 | 0.00063011 | 0.00063011 | 0.00011595 | 0.00074967 | 0.00074967 | 0.00074967 | 0.00074967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8845.632 | 8845.7997 | 8970.6931 | 8676.9024 | 8676.9024 | 9034.5235 | 8440.009 | 0 | 0 | 0 | 0 | 0 | 0 | -1.07 | 75.7876 | 75.7876 | 75.7876 | 75.7876 | -1.0715 | 75.7862 | 75.7862 | 75.7862 | 75.7862 | 0 | 74.3406 | 74.3406 | 74.3406 | 74.3406 | 5.0936 | 77.4046 | 77.4046 | 77.4046 | 77.4046 | 0 | 0 | 0 | 0
EPr | 3 |  | 297865.1875 | 294322.125 | 279018.0938 | 293975.0938 | 291484.9375 | 296749.5625 | 291104.9688 | 339935.9375 | 334130.5 | 329078.1562 | 332385.5625 | 327171.5312 | 322717.4062 | 100.5203 | 100.5203 | 100.5203 | 100.5203 | 100.5203 | 100.5203 | CZ03 | 152.2482 | -453.7771 | -396.0232 | -378.6642 | -282.483 | 187.4954 | -418.5299 | -310.5141 | -343.4169 | -247.2358 | 24.7727 | -457.2295 | -399.4756 | -382.1165 | -285.9354 | 56.1538 | -429.6284 | -321.6126 | -354.5154 | -258.3343 | 57.7539 | 108.0158 | 51.8704 | 96.1811 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7721.6902 | 7721.8221 | 7938.6842 | 7652.6093 | 7652.6093 | 8071.6461 | 7609.3088 | 0 | 0 | 0 | 0 | 0 | 0 | -2.1574 | 76.8185 | 76.8185 | 76.8185 | 76.8185 | -2.1587 | 76.8172 | 76.8172 | 76.8172 | 76.8172 | 0 | 76.13 | 76.13 | 76.13 | 76.13 | 4.5994 | 80.2987 | 80.2987 | 80.2987 | 80.2987 | 0 | 0 | 0 | 0
EPr | 4 |  | 318485.2188 | 314668.5 | 295356.5312 | 317213.5 | 311164.6875 | 319715.625 | 308926.0625 | 354592.1875 | 347043.4375 | 340567.4062 | 345854.6875 | 339109.5312 | 333275.8125 | 109.0204 | 109.0206 | 109.0206 | 109.0204 | 109.0206 | 109.0206 | CZ04 | 177.1408 | -366.2037 | -296.9617 | -286.0582 | -170.6771 | 212.15 | -331.1945 | -202.5507 | -251.049 | -135.6679 | 55.4833 | -342.8595 | -273.6175 | -262.714 | -147.3329 | 98.9683 | -319.9085 | -191.2647 | -239.763 | -124.3819 | 69.2415 | 128.6434 | 61.8705 | 115.3808 | 173.8252 | 173.8242 | 154.7164 | 187.3276 | 170.9912 | 188.1511 | 163.979 | 182.5331 | 172.2173 | 163.3393 | 174.3795 | 165.2983 | 156.1986 | 0.17527 | -0.079884 | 0.096174 | -0.0050941 | 0.16167 | 0.17528 | -0.079874 | 0.096183 | -0.0050847 | 0.16168 | 0.14985 | 0.043978 | 0.22003 | 0.11877 | 0.28553 | 0.22172 | 0.051531 | 0.22759 | 0.12632 | 0.29309 | 0.094623 | 0.17606 | 0.083298 | 0.16677 | 6391.7248 | 6391.8611 | 6551.4387 | 6314.2317 | 6314.2317 | 6769.8176 | 6337.2698 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4637 | 58.6299 | 58.6299 | 58.6299 | 58.6299 | -1.465 | 58.6287 | 58.6286 | 58.6287 | 58.6286 | 0 | 57.9179 | 57.9178 | 57.9179 | 57.9178 | 3.9676 | 62.0968 | 62.0967 | 62.0968 | 62.0967 | 0 | 0 | 0 | 0
EPr | 5 |  | 295413.375 | 293798.8438 | 279789.3125 | 294716.0625 | 291611.7812 | 303127.3125 | 296602.0938 | 343380.3438 | 337134.375 | 331704.5938 | 335575.75 | 329972.75 | 325121.8438 | 90.7995 | 90.7995 | 90.7995 | 90.7995 | 90.7995 | 90.7995 | CZ05 | 154.2908 | -546.0546 | -477.266 | -460.1005 | -344.9687 | 172.0721 | -528.2733 | -399.6851 | -442.3192 | -327.1875 | 34.1883 | -535.953 | -467.1644 | -449.9989 | -334.8672 | 71.864 | -443.3176 | -314.7294 | -357.3635 | -242.2318 | 68.7886 | 128.5882 | 61.7074 | 115.1317 | 123.9866 | 123.8822 | 112.9536 | 127.581 | 120.8216 | 131.86 | 121.6198 | 128.2902 | 123.7844 | 119.9089 | 124.3877 | 119.4398 | 116.4475 | 0.12036 | -0.048546 | 0.043759 | -0.0055669 | 0.081881 | 0.12151 | -0.047396 | 0.044909 | -0.0044172 | 0.083031 | 0.074443 | -0.0078112 | 0.084494 | 0.035168 | 0.12262 | 0.11278 | 0.039315 | 0.13162 | 0.082294 | 0.16974 | 0.049624 | 0.092305 | 0.054493 | 0.087448 | 7986.5568 | 7986.6573 | 8209.9104 | 7963.6691 | 7963.6691 | 8339.2 | 7818.0685 | 0 | 0 | 0 | 0 | 0 | 0 | -2.4587 | 87.9592 | 87.9592 | 87.9592 | 87.9592 | -2.4599 | 87.9581 | 87.9581 | 87.9581 | 87.9581 | 0 | 87.7061 | 87.7061 | 87.7061 | 87.7061 | 5.7394 | 91.8419 | 91.8419 | 91.8419 | 91.8419 | 0 | 0 | 0 | 0
EPr | 6 |  | 322701.375 | 317832.8125 | 299095.3438 | 322651.0625 | 315879.2188 | 326026.9375 | 314027.6875 | 341700.0312 | 335362.75 | 329928.0312 | 335063.0312 | 329384.3125 | 324558.4688 | 117.9333 | 117.9333 | 117.9333 | 117.9333 | 117.9333 | 117.9333 | CZ06 | 158.8818 | -202.3789 | -148.6428 | -146.1013 | -57.0293 | 200.1642 | -161.0966 | -61.2775 | -104.819 | -15.747 | 57.4209 | -161.5232 | -107.787 | -105.2456 | -16.1736 | 101.746 | -132.8979 | -33.0788 | -76.6203 | 12.4517 | 53.7361 | 99.8191 | 48.1519 | 89.072 | 161.1535 | 161.1534 | 146.1448 | 174.1384 | 160.0915 | 177.0567 | 156.3724 | 165.5972 | 156.5564 | 149.0937 | 158.9985 | 150.7964 | 144.0569 | 0.12726 | -0.037681 | 0.10226 | 0.018272 | 0.14497 | 0.12726 | -0.03768 | 0.10226 | 0.018273 | 0.14497 | 0.11911 | 0.072424 | 0.21236 | 0.12838 | 0.25507 | 0.17539 | 0.09717 | 0.23711 | 0.15312 | 0.27982 | 0.076661 | 0.13994 | 0.069549 | 0.1267 | 4153.6163 | 4153.7789 | 4286.1533 | 4098.6614 | 4098.6614 | 4535.9648 | 4339.1235 | 0 | 0 | 0 | 0 | 0 | 0 | -1.1225 | 35.2214 | 35.2214 | 35.2214 | 35.2214 | -1.1238 | 35.22 | 35.22 | 35.22 | 35.22 | 0 | 34.754 | 34.754 | 34.754 | 34.754 | 1.6691 | 38.4621 | 38.4621 | 38.4621 | 38.4621 | 0 | 0 | 0 | 0
EPr | 7 |  | 318887.0625 | 310765.7188 | 292307.1875 | 313670.5625 | 308726.9375 | 315993.7188 | 306388.8125 | 331790.1875 | 326678.2812 | 322322.1562 | 326292.4375 | 321695.1562 | 317787.3438 | 136.1879 | 136.1879 | 136.1879 | 136.1879 | 136.1879 | 136.1879 | CZ07 | 135.5372 | -154.3784 | -116.8427 | -114.0095 | -51.5584 | 195.1706 | -94.745 | -25.2232 | -54.3762 | 8.075 | 36.3 | -133.0487 | -95.513 | -92.6799 | -30.2287 | 70.5269 | -115.9903 | -46.4684 | -75.6214 | -13.1702 | 37.5357 | 69.5218 | 33.7569 | 62.4512 | 148.1381 | 148.1381 | 133.7056 | 157.6978 | 146.3116 | 160.2012 | 143.5844 | 145.8362 | 139.5118 | 134.186 | 139.5154 | 133.9307 | 129.2277 | 0.10597 | 0.016902 | 0.10245 | 0.063315 | 0.13885 | 0.10597 | 0.016902 | 0.10245 | 0.063315 | 0.13885 | 0.083607 | 0.087097 | 0.17264 | 0.13351 | 0.20905 | 0.12201 | 0.10548 | 0.19102 | 0.15189 | 0.22743 | 0.046439 | 0.085545 | 0.041007 | 0.07554 | 3347.7354 | 3348.015 | 3463.1341 | 3261.9158 | 3261.9158 | 3641.8874 | 3648.9994 | 0 | 0 | 0 | 0 | 0 | 0 | -0.8453 | 24.5838 | 24.5838 | 24.5838 | 24.5838 | -0.84735 | 24.5817 | 24.5817 | 24.5817 | 24.5817 | 0 | 23.9516 | 23.9516 | 23.9516 | 23.9516 | -0.052222 | 26.7416 | 26.7416 | 26.7416 | 26.7416 | 0 | 0 | 0 | 0
EPr | 8 |  | 351793.125 | 341764.625 | 314183.9062 | 345683.2812 | 337188.875 | 344921.75 | 329728.9062 | 356049.6562 | 348401.75 | 341910.1562 | 347836.0625 | 340989.75 | 335180.0625 | 156.0668 | 156.0668 | 156.0668 | 156.0668 | 156.0668 | 156.0668 | CZ08 | 176.7238 | -91.5315 | -42.5275 | -38.9028 | 42.1907 | 240.9816 | -27.2738 | 63.3253 | 25.3549 | 106.4484 | 54.428 | -66.4227 | -17.4186 | -13.794 | 67.2995 | 97.3483 | -71.3022 | 19.2968 | -18.6735 | 62.42 | 49.0041 | 90.599 | 43.8678 | 81.0935 | 190.0202 | 190.0201 | 164.5706 | 200.6805 | 182.6414 | 199.2999 | 173.9864 | 186.5554 | 175.4443 | 165.981 | 173.916 | 164.281 | 156.1852 | 0.16307 | 0.0222 | 0.15403 | 0.10319 | 0.2168 | 0.16307 | 0.022201 | 0.15403 | 0.10319 | 0.2168 | 0.11559 | 0.090506 | 0.22234 | 0.17149 | 0.2851 | 0.1622 | 0.081661 | 0.21349 | 0.16265 | 0.27626 | 0.071194 | 0.13183 | 0.061737 | 0.11361 | 3626.3747 | 3626.592 | 3721.4838 | 3496.633 | 3496.633 | 3877.632 | 3766.8125 | 0 | 0 | 0 | 0 | 0 | 0 | -0.60802 | 23.2374 | 23.2374 | 23.2374 | 23.2374 | -0.60941 | 23.236 | 23.236 | 23.236 | 23.236 | 0 | 22.4047 | 22.4047 | 22.4047 | 22.4047 | 0.71008 | 24.846 | 24.846 | 24.846 | 24.846 | 0 | 0 | 0 | 0
EPr | 9 |  | 362552.0938 | 352479.625 | 319663.8125 | 355047.4688 | 345738.0938 | 351132.2812 | 333979.75 | 364528.625 | 355941.625 | 348645.0312 | 355064.75 | 347404.9375 | 340926.875 | 158.5477 | 158.5477 | 158.5477 | 158.5477 | 158.5477 | 158.5477 | CZ09 | 206.9775 | -75.996 | -21.8357 | -16.305 | 72.8661 | 270.5071 | -12.4665 | 87.7153 | 47.2245 | 136.3956 | 58.7165 | -59.8 | -5.6397 | -0.109 | 89.0621 | 108.1853 | -84.4941 | 15.6877 | -24.8031 | 64.368 | 54.1604 | 100.1818 | 48.3123 | 89.1711 | 229.6223 | 229.6222 | 192.2532 | 245.2671 | 220.076 | 241.8767 | 205.5552 | 226.7763 | 210.7884 | 197.3702 | 208.2677 | 194.5599 | 183.0398 | 0.2357 | 0.01795 | 0.20342 | 0.13469 | 0.29381 | 0.2357 | 0.01795 | 0.20342 | 0.13469 | 0.29381 | 0.15889 | 0.11663 | 0.3021 | 0.23336 | 0.39248 | 0.22909 | 0.095242 | 0.28071 | 0.21198 | 0.3711 | 0.10084 | 0.18547 | 0.086459 | 0.15912 | 4034.9226 | 4035.2272 | 4130.7277 | 3863.5501 | 3863.5501 | 4251.8867 | 4124.7856 | 0 | 0 | 0 | 0 | 0 | 0 | -0.60235 | 25.4512 | 25.4512 | 25.4512 | 25.4512 | -0.60427 | 25.4493 | 25.4493 | 25.4493 | 25.4493 | 0 | 24.3684 | 24.3684 | 24.3684 | 24.3684 | 0.80166 | 26.8177 | 26.8177 | 26.8177 | 26.8177 | 0 | 0 | 0 | 0
EPr | 10 |  | 357811.5 | 350260.3125 | 321169.9688 | 355116.4375 | 344464.0938 | 354238.3438 | 336033.1875 | 368788.875 | 359285.0625 | 351214.1562 | 359537.4062 | 351004.0312 | 343753.375 | 125.7551 | 125.7551 | 125.7551 | 125.7551 | 125.7551 | 125.7551 | CZ10 | 231.3254 | -147.3385 | -71.7645 | -73.7711 | 51.7429 | 291.3722 | -87.2917 | 52.4619 | -13.7243 | 111.7897 | 84.7071 | -108.7228 | -33.1488 | -35.1554 | 90.3587 | 144.7668 | -115.7053 | 24.0482 | -42.138 | 83.3761 | 75.574 | 139.7536 | 67.8571 | 125.5141 | 228.7642 | 228.764 | 197.7381 | 249.5345 | 223.4107 | 241.9881 | 205.3067 | 253.1601 | 233.2884 | 216.5591 | 240.8104 | 222.5002 | 207.3084 | 0.24672 | -0.194 | 0.097053 | -0.095793 | 0.17061 | 0.24672 | -0.194 | 0.097054 | -0.095791 | 0.17062 | 0.20774 | -0.028831 | 0.26222 | 0.069373 | 0.33578 | 0.29169 | -0.088839 | 0.20221 | 0.0093649 | 0.27577 | 0.15802 | 0.29105 | 0.1456 | 0.26641 | 4197.0883 | 4197.2547 | 4293.3171 | 4078.9082 | 4078.9082 | 4427.9718 | 4245.3952 | 0 | 0 | 0 | 0 | 0 | 0 | -0.76388 | 33.3764 | 33.3764 | 33.3764 | 33.3764 | -0.76521 | 33.3751 | 33.3751 | 33.3751 | 33.3751 | 0 | 32.4353 | 32.4353 | 32.4353 | 32.4353 | 1.4518 | 35.2111 | 35.2111 | 35.2111 | 35.2111 | 0 | 0 | 0 | 0
EPr | 11 |  | 351149.5312 | 346332.3125 | 318098.5 | 352429.8438 | 342450.375 | 352964.2188 | 335677.1562 | 388574.7188 | 377554.4688 | 367959.0938 | 377282.875 | 367227.0938 | 358599.6875 | 121.0254 | 121.0254 | 121.0254 | 121.0254 | 121.0254 | 121.0254 | CZ11 | 233.2883 | -349.0375 | -257.9802 | -255.7361 | -101.362 | 273.0917 | -309.2341 | -138.8928 | -215.9327 | -61.5586 | 82.4576 | -298.6553 | -207.5979 | -205.3538 | -50.9797 | 142.8383 | -294.2399 | -123.8986 | -200.9384 | -46.5643 | 91.0573 | 170.3413 | 83.0882 | 154.3741 | 16.2798 | 16.2798 | 13.7919 | 21.9794 | 19.2103 | 38.3637 | 30.1463 | 15.9982 | 14.3217 | 12.8646 | 17.1767 | 15.4466 | 13.9421 | 0.020557 | 0.0023265 | 0.028219 | -0.0074105 | 0.019316 | 0.020557 | 0.0023266 | 0.028219 | -0.0074103 | 0.019316 | 0.02288 | 0.049421 | 0.075313 | 0.039684 | 0.06641 | 0.067898 | 0.1848 | 0.21069 | 0.17506 | 0.20179 | 0.013853 | 0.025892 | 0.014295 | 0.026726 | 8157.3587 | 8157.4829 | 8282.2406 | 7960.4531 | 7960.4531 | 8227.1232 | 7705.3958 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0308 | 67.4031 | 67.4031 | 67.4031 | 67.4031 | -1.0319 | 67.402 | 67.402 | 67.402 | 67.402 | 0 | 65.7751 | 65.7751 | 65.7751 | 65.7751 | 4.3109 | 67.9785 | 67.9785 | 67.9785 | 67.9785 | 0 | 0 | 0 | 0
EPr | 12 |  | 337428.875 | 332329.0938 | 307145.3125 | 334985.1562 | 327207.0312 | 332526.6562 | 319093.9688 | 374748.1562 | 365158 | 356953.8125 | 363983.9375 | 355474.875 | 348131.3125 | 119.3028 | 119.3028 | 119.3028 | 119.3028 | 119.3028 | 119.3028 | CZ12 | 211.0913 | -355.558 | -275.173 | -265.332 | -132.4547 | 253.8378 | -312.8115 | -163.6587 | -222.5854 | -89.7082 | 65.1965 | -333.2948 | -252.9098 | -243.0688 | -110.1915 | 112.5932 | -353.902 | -204.7493 | -263.676 | -130.7988 | 80.385 | 149.1528 | 71.3233 | 132.8772 | 5.7744 | 5.7744 | 5.0026 | 7.7039 | 6.897 | 17.5837 | 14.3388 | 6.0218 | 5.5019 | 5.081 | 6.598 | 6.0129 | 5.5356 | 0.0064693 | -0.0020735 | 0.0058119 | -0.0069032 | 0.002002 | 0.0064696 | -0.0020733 | 0.0058122 | -0.0069029 | 0.0020022 | 0.0067631 | 0.0141 | 0.021985 | 0.0092699 | 0.018175 | 0.027199 | 0.096912 | 0.1048 | 0.092083 | 0.10099 | 0.0043575 | 0.0078854 | 0.0049045 | 0.0089052 | 7997.0394 | 7997.3024 | 8116.7366 | 7830.2746 | 7830.2746 | 8122.2406 | 7599.8131 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0011 | 67.0337 | 67.0337 | 67.0337 | 67.0337 | -1.0033 | 67.0315 | 67.0315 | 67.0315 | 67.0315 | 0 | 65.6336 | 65.6336 | 65.6336 | 65.6336 | 4.379 | 68.0809 | 68.0809 | 68.0809 | 68.0809 | 0 | 0 | 0 | 0
EPr | 13 |  | 354663.5 | 349502.1875 | 321351.5 | 355574.3438 | 344481.0312 | 354694.5312 | 336529.1875 | 390094.9375 | 378599 | 368770 | 378728.875 | 368326.9375 | 359527.75 | 125.4383 | 125.4383 | 125.4383 | 125.4383 | 125.4383 | 125.4383 | CZ13 | 224.4186 | -323.6073 | -231.9612 | -232.9966 | -79.9243 | 265.5649 | -282.4611 | -112.4577 | -191.8503 | -38.778 | 88.4364 | -275.1998 | -183.5537 | -184.589 | -31.5167 | 144.815 | -282.2137 | -112.2103 | -191.6029 | -38.5307 | 91.6462 | 170.0034 | 82.9247 | 153.0723 | 14.6044 | 14.6045 | 12.1975 | 19.2257 | 16.8088 | 34.0875 | 28.0926 | 15.3945 | 13.9327 | 12.7246 | 16.9038 | 15.2168 | 13.7987 | 0.019189 | -0.0062984 | 0.014986 | -0.01833 | 0.0064239 | 0.019188 | -0.0062987 | 0.014986 | -0.018331 | 0.0064236 | 0.019268 | 0.030542 | 0.051827 | 0.01851 | 0.043264 | 0.047792 | 0.14902 | 0.17031 | 0.13699 | 0.16174 | 0.011654 | 0.021285 | 0.013449 | 0.024754 | 7330.8685 | 7331.0035 | 7452.3302 | 7192.007 | 7192.007 | 7389.5168 | 6907.0464 | 0 | 0 | 0 | 0 | 0 | 0 | -0.96722 | 58.4431 | 58.4431 | 58.4431 | 58.4431 | -0.9683 | 58.442 | 58.442 | 58.442 | 58.442 | 0 | 57.335 | 57.335 | 57.335 | 57.335 | 3.8463 | 58.9096 | 58.9096 | 58.9096 | 58.9096 | 0 | 0 | 0 | 0
EPr | 14 |  | 365205.6562 | 359812 | 327148.4062 | 363268.3438 | 351699.5 | 361713.1875 | 342584.5312 | 399336.9375 | 387144.7812 | 376766.4375 | 386677.9375 | 375673.25 | 366304.8125 | 133.3594 | 133.3594 | 133.2487 | 133.3594 | 133.3594 | 133.2487 | CZ14 | 244.9291 | -296.3791 | -205.1261 | -201.4552 | -48.727 | 285.3736 | -255.9346 | -86.7609 | -161.0107 | -8.2489 | 86.7494 | -270.4616 | -179.187 | -175.5377 | -22.788 | 143.4369 | -282.123 | -112.9711 | -187.1991 | -34.4591 | 91.4233 | 169.3863 | 82.519 | 152.8955 | 224.6318 | 224.6312 | 194.8091 | 241.3034 | 216.4572 | 238.6955 | 203.9616 | 223.7777 | 208.0271 | 195.1109 | 211.9917 | 197.976 | 186.3643 | 0.22362 | 0.0064003 | 0.22154 | 0.094778 | 0.28718 | 0.22363 | 0.0064045 | 0.22155 | 0.094782 | 0.28719 | 0.18631 | 0.13142 | 0.34666 | 0.21979 | 0.41231 | 0.26045 | 0.11186 | 0.32709 | 0.20024 | 0.39273 | 0.11811 | 0.21514 | 0.1051 | 0.19233 | 8267.3939 | 8267.5168 | 8324.4973 | 8027.5354 | 8027.5354 | 8330.5222 | 7763.0349 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42727 | 61.9943 | 62.0458 | 61.9943 | 62.0458 | -0.42819 | 61.9933 | 62.0448 | 61.9933 | 62.0448 | 0 | 60.1948 | 60.2448 | 60.1948 | 60.2448 | 4.2553 | 62.4667 | 62.5186 | 62.4667 | 62.5186 | 0 | 0 | 0 | 0
EPr | 15 |  | 453170.625 | 445083.875 | 392973.75 | 458963.5 | 432743.375 | 461417.4062 | 420406.3438 | 442620.75 | 424414.9688 | 409086.0625 | 428500.75 | 411868.5 | 397890.625 | 153.6837 | 153.6837 | 153.6837 | 153.6837 | 153.6837 | 153.6837 | CZ15 | 339.0739 | 16.0272 | 134.4899 | 107.9043 | 307.0805 | 391.6934 | 68.6467 | 286.8526 | 160.5237 | 359.6999 | 170.611 | 106.3402 | 224.8029 | 198.2172 | 397.3934 | 266.8538 | 122.3074 | 340.5134 | 214.1845 | 413.3607 | 118.4627 | 218.2059 | 108.2239 | 199.1762 | 264.7997 | 264.7997 | 225.4996 | 287.2897 | 255.1351 | 277.7099 | 233.3111 | 277.119 | 254.8702 | 236.2355 | 253.1359 | 233.9241 | 217.8033 | 0.25572 | -0.08016 | 0.18586 | 0.075895 | 0.3058 | 0.25572 | -0.08016 | 0.18586 | 0.075895 | 0.3058 | 0.20923 | 0.066179 | 0.3322 | 0.22223 | 0.45214 | 0.2889 | 0.0038452 | 0.26987 | 0.1599 | 0.3898 | 0.14477 | 0.26602 | 0.12501 | 0.2299 | 1798.5955 | 1798.6803 | 1856.1144 | 1720.9064 | 1720.9064 | 1951.7909 | 1934.2947 | 0 | 0 | 0 | 0 | 0 | 0 | -0.37372 | 11.7038 | 11.7038 | 11.7038 | 11.7038 | -0.37427 | 11.7032 | 11.7032 | 11.7032 | 11.7032 | 0 | 11.1977 | 11.1977 | 11.1977 | 11.1977 | 0.11385 | 12.7001 | 12.7001 | 12.7001 | 12.7001 | 0 | 0 | 0 | 0
EPr | 16 |  | 290770.4062 | 290113.9062 | 276966.1562 | 290939.625 | 288481.0938 | 300650.2812 | 296207.1875 | 425960.4062 | 412711.375 | 401133.25 | 407891.8438 | 395978.9375 | 385390.5938 | 92.0927 | 92.0927 | 92.0927 | 92.0927 | 92.0927 | 92.0927 | CZ16 | 142.7665 | -1475.1068 | -1331.2405 | -1278.907 | -1034.5743 | 149.8952 | -1467.9782 | -1198.3893 | -1271.7783 | -1027.4456 | 26.6963 | -1466.1407 | -1322.2743 | -1269.9408 | -1025.6081 | 48.2459 | -1360.6962 | -1091.1073 | -1164.4964 | -920.1637 | 143.8663 | 269.5889 | 129.3578 | 244.3327 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 1.6302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19216.5824 | 19216.6131 | 19570.5254 | 19258.4576 | 19258.4576 | 18802.6611 | 17290.4166 | 0 | 0 | 0 | 0 | 0 | 0 | -3.843 | 208.6661 | 208.6661 | 208.6661 | 208.6661 | -3.8433 | 208.6658 | 208.6658 | 208.6658 | 208.6658 | 0 | 209.1205 | 209.1205 | 209.1205 | 209.1205 | 16.4209 | 204.1711 | 204.1711 | 204.1711 | 204.1711 | 0 | 0 | 0 | 0
|  |  | Baseline is One Speed T-24 AC/Furnace, < 65 kBtuh, with economizer | [8 empty] | Baseline is One Speed T-24 AC/Furnace, < 65 kBtuh, without economizer | [10 empty] | Baseline is 2 Speed T-24 AC/Furnace, 65-135 kBtuh | [7 empty] | Baseline is T-24 PVAV/Gas Boiler | [7 empty] | Baseline is T-24 Heat Pump VRF System | [9 empty] | Baseline is T-24 Heat Recovery VRF System
-1475.1068
413.3607
-0.194
0.45214
-4.7372
209.1205

## OfL_Svgs
|  |  |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 25 | 25 | 25 | 25 | 25 | 25 | [15 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | CoolCap | CoolCap | CoolCap | CoolCap | CoolCap | CoolCap |  |  | Baseline is FPFC w/ T-24 Chlr and Blr |  |  |  |  | Baseline is 2 Speed T-24 AC/Furnace, |  |  |  | Baseline is T24 Heat Pump VRF System |  |  |  | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer |  | Baseline is FPFC w/ T-24 Chlr and Blr |  |  |  | Baseline is T24 Single-Mode VRF System, |  |  |  | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating |  | Baseline is One Speed T-24 AC/Furnace, |  |  |  |  | Baseline is T24 Single-Mode VRF System,
|  |  | Sys ID | FPFC_1 | FPFC_2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 | [7 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | Baseline is T24 Heat Recovery VRF System |  | FPFC_1 | FPFC_2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 | [5 empty] | 14 | tons/system |  |  | FPFC_1 | FPFC_2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 |  | < 65 kBtuh |  |  |  |  | 14 | tons/system
Run ID | Bldg | CZ | [15 empty] | CZ | Hi Eff FPFC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 |  | VRF HP Std | VRF HP Tier2 | VRF HR Std | VRF HR Tier2 | VRF HP Tier1 | VRF HP Tier2 | VRF HR Tier1 | VRF HR Tier2 | [8 empty] | Hi Eff FPFC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP Tier1 | VRF HP Tier2 | VRF HR Tier1 | VRF HR Tier2 | [8 empty] | Hi Eff FPFC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | 0 | VRF HP Tier1 | VRF HP Tier2 | VRF HR Tier1 | VRF HR Tier2
| OfL | 1 |  | 1613998.875 | 1583070.75 | 1572293.75 | 1553170.875 | 1542469.25 | 1563456.25 | 1545688.875 | 1536101.5 | 285.1902 | 285.1902 | 285.1902 | 285.878 | 285.878 | 285.878 | CZ01 | 108.4474 | 146.2362 | 250.8137 | 176.7979 | 272.4847 | [5 empty] | 67.0531 | 104.5776 | 93.0637 | 126.6003 | 433.5292 | 415.1813 | 438.3591 | 420.0178 | 409.5473 | 436.3544 | 418.3131 | 407.1448 | 0.064336 | -0.016936 | 0.084091 | -0.0098827 | 0.092292 | 0.064312 | 0.10103 | 0.063108 | 0.10218 | 6737.8342 | 4347.4989 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3815 | 23.6258 | 23.6258 | 23.5689 | 23.5689 |  | 0 | 0 | 0 | 0
| OfL | 2 |  | 1754176.375 | 1700038.25 | 1706650.125 | 1665167.75 | 1642262.375 | 1691293.5 | 1652487.75 | 1631300.625 | 370.8176 | 370.8176 | 370.8176 | 382.7056 | 382.7056 | 382.7056 | CZ02 | 145.9966 | 128.1661 | 301.8034 | 164.3114 | 321.0712 | [5 empty] | 111.8673 | 173.6373 | 141.5249 | 196.8863 | 509.712 | 484.0682 | 640.9734 | 585.6895 | 555.5587 | 646.5062 | 591.2188 | 560.7246 | 0.069155 | -0.35398 | -0.12364 | -0.35744 | -0.13329 | 0.14909 | 0.23034 | 0.14446 | 0.22415 | 5394.6714 | 2987.0998 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4926 | 14.548 | 14.548 | 14.0961 | 14.0961 |  | 0 | 0 | 0 | 0
| OfL | 3 |  | 1710957.375 | 1662125.75 | 1651887 | 1619044.375 | 1600921.125 | 1640503.5 | 1609612 | 1592671.625 | 344.5885 | 344.5885 | 344.5885 | 345.4191 | 345.4191 | 345.4191 | CZ03 | 141.7099 | 171.4229 | 319.3265 | 203.9664 | 342.4413 | [5 empty] | 95.3097 | 147.9036 | 122.3876 | 171.4305 | 475.8599 | 452.936 | 509.9232 | 478.9447 | 461.8945 | 508.9862 | 478.1314 | 461.149 | 0.066525 | -0.098852 | 0.040528 | -0.095902 | 0.042589 | 0.0899 | 0.13938 | 0.089326 | 0.13849 | 3364.6726 | 1775.1571 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6128 | 9.7643 | 9.7643 | 9.7408 | 9.7408 |  | 0 | 0 | 0 | 0
| OfL | 4 |  | 1774178.25 | 1715996.5 | 1721443 | 1676628.125 | 1652924.625 | 1707524.25 | 1665430.125 | 1642464.75 | 344.7882 | 344.7882 | 341.2383 | 351.4517 | 351.4517 | 351.4517 | CZ04 | 168.7463 | 152.9497 | 355.3342 | 189.6534 | 374.7699 | [5 empty] | 129.978 | 200.7933 | 159.3758 | 224.7201 | 509.7171 | 484.3884 | 617.9565 | 567.2574 | 544.3799 | 624.8077 | 567.3309 | 535.7767 | 0.073462 | -0.31393 | -0.10158 | -0.32747 | -0.074149 | 0.14704 | 0.21562 | 0.16354 | 0.25332 | 3547.9661 | 1902.7587 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7716 | 10.2903 | 10.3973 | 10.0952 | 10.0952 |  | 0 | 0 | 0 | 0
| OfL | 5 |  | 1698153.75 | 1651819 | 1652499.75 | 1618959 | 1600438 | 1640997.75 | 1609156.125 | 1591693.375 | 311.0145 | 311.0145 | 311.0145 | 305.3857 | 305.3857 | 305.3857 | CZ05 | 148.9794 | 146.7906 | 314.1839 | 187.16 | 348.6095 | [5 empty] | 107.843 | 167.3933 | 141.9307 | 199.1133 | 453.487 | 431.7918 | 483.8961 | 457.5725 | 442.9832 | 481.0333 | 455.0973 | 440.8018 | 0.069756 | -0.097774 | 0.033773 | -0.090202 | 0.041538 | 0.084638 | 0.13155 | 0.084928 | 0.13174 | 3300.3635 | 1831.8806 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7216 | 10.6116 | 10.6116 | 10.8072 | 10.8072 |  | 0 | 0 | 0 | 0
| OfL | 6 |  | 1788755.875 | 1729221.875 | 1748237 | 1698959.125 | 1671821 | 1725647.625 | 1680286.5 | 1655348.875 | 370.646 | 370.646 | 370.646 | 377.4116 | 377.4116 | 377.4116 | CZ06 | 160.6223 | 109.3196 | 315.4894 | 167.2133 | 353.4788 | [5 empty] | 132.9513 | 206.1698 | 180.0435 | 246.1189 | 504.3471 | 478.2634 | 571.913 | 529.96 | 506.932 | 571.5601 | 530.3149 | 507.517 | 0.070374 | -0.18229 | -0.006974 | -0.17809 | -0.0083991 | 0.11319 | 0.17532 | 0.10928 | 0.16969 | 2137.1117 | 1046.4273 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9427 | 5.7659 | 5.7659 | 5.6625 | 5.6625 |  | 0 | 0 | 0 | 0
| OfL | 7 |  | 1791413.25 | 1730617.25 | 1734554 | 1687503 | 1661581.625 | 1717497 | 1673210.5 | 1648873.375 | 369.4076 | 369.4076 | 369.4076 | 359.2355 | 359.2355 | 359.2355 | CZ07 | 164.577 | 153.9201 | 351.459 | 205.7599 | 396.7867 | [5 empty] | 127.3688 | 197.5389 | 170.7613 | 238.5083 | 499.7202 | 474.728 | 543.9774 | 507.5477 | 487.4075 | 547.4134 | 510.4171 | 489.9534 | 0.067655 | -0.11981 | 0.033331 | -0.13276 | 0.027188 | 0.098617 | 0.15314 | 0.10299 | 0.15995 | 1100.4283 | 495.9742 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6363 | 2.9789 | 2.9789 | 3.0633 | 3.0633 |  | 0 | 0 | 0 | 0
| OfL | 8 |  | 1828623.5 | 1762827.875 | 1785899.375 | 1729977 | 1699156 | 1763648 | 1712165 | 1683870.875 | 377.0514 | 377.0514 | 377.0514 | 405.4829 | 405.4829 | 405.4829 | CZ08 | 174.5004 | 113.3111 | 343.3683 | 160.2423 | 356.9882 | [5 empty] | 148.315 | 230.0572 | 181.8434 | 251.6222 | 510.8841 | 483.7025 | 603.8354 | 556.37 | 530.2334 | 599.7673 | 553.1279 | 527.4609 | 0.07209 | -0.24652 | -0.051317 | -0.2192 | -0.040882 | 0.12589 | 0.1952 | 0.11502 | 0.17832 | 1424.3074 | 679.8306 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9745 | 3.7775 | 3.7775 | 3.5126 | 3.5126 |  | 0 | 0 | 0 | 0
| OfL | 9 |  | 1891440.625 | 1809484.375 | 1812363.25 | 1753191.125 | 1720595.5 | 1783016.125 | 1729189.625 | 1699684 | 440.9666 | 440.9666 | 440.9666 | 445.6552 | 445.6552 | 445.6552 | CZ09 | 185.8559 | 179.3274 | 387.4333 | 243.2923 | 430.2802 | [5 empty] | 134.1873 | 208.1059 | 186.6322 | 252.8395 | 562.4598 | 530.6568 | 723.0115 | 654.3314 | 616.5828 | 697.2673 | 633.4772 | 598.3779 | 0.072121 | -0.36409 | -0.12274 | -0.30249 | -0.080596 | 0.15575 | 0.24135 | 0.14314 | 0.2219 | 2025.6363 | 973.1693 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3867 | 4.5936 | 4.5936 | 4.5453 | 4.5453 |  | 0 | 0 | 0 | 0
| OfL | 10 |  | 1851987 | 1783293.625 | 1825547.5 | 1763459.875 | 1729282 | 1804381.875 | 1746165.25 | 1714238.25 | 413.1131 | 413.1131 | 413.1131 | 421.426 | 421.426 | 421.426 | CZ10 | 166.2823 | 64.0006 | 297.0252 | 112.962 | 326.8634 | [5 empty] | 150.2921 | 233.0246 | 188.3658 | 264.1252 | 541.8077 | 513.4553 | 738.1511 | 666.1469 | 626.6702 | 750.4159 | 675.9462 | 635.1567 | 0.068631 | -0.47528 | -0.20542 | -0.49501 | -0.22151 | 0.1743 | 0.26986 | 0.17671 | 0.2735 | 2283.0091 | 1118.744 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8183 | 5.5264 | 5.5264 | 5.4173 | 5.4173 |  | 0 | 0 | 0 | 0
| OfL | 11 |  | 1842696.5 | 1776374.375 | 1820022.75 | 1759258.375 | 1725780.75 | 1805504.375 | 1747130.125 | 1715311 | 403.8562 | 403.8562 | 403.8562 | 404.4992 | 404.4992 | 404.4992 | CZ11 | 164.2221 | 56.1431 | 289.4985 | 91.9461 | 314.9215 | [5 empty] | 150.4604 | 233.3553 | 180.2046 | 258.8676 | 527.7437 | 496.7815 | 693.4312 | 629.5374 | 594.394 | 694.1595 | 630.1627 | 595.0364 | 0.076666 | -0.41026 | -0.16503 | -0.41141 | -0.16636 | 0.15821 | 0.24523 | 0.15821 | 0.24505 | 5134.921 | 3017.1558 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2439 | 12.7147 | 12.7147 | 12.6945 | 12.6945 |  | 0 | 0 | 0 | 0
| OfL | 12 |  | 1824632.375 | 1757293 | 1770493.125 | 1718477.75 | 1689773.5 | 1749842.75 | 1701565.75 | 1675156.625 | 407.2503 | 407.2503 | 407.2503 | 420.6476 | 420.6476 | 420.6476 | CZ12 | 165.3513 | 132.9385 | 331.1449 | 177.7964 | 355.3467 | [5 empty] | 127.7234 | 198.2064 | 163.8601 | 226.6422 | 527.6898 | 498.3108 | 662.7319 | 604.6044 | 572.6025 | 641.9423 | 587.7536 | 557.9487 | 0.07214 | -0.3316 | -0.11028 | -0.27161 | -0.071934 | 0.14273 | 0.22131 | 0.12882 | 0.19968 | 4329.0272 | 2556.9696 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3513 | 10.6299 | 10.6299 | 10.2913 | 10.2913 |  | 0 | 0 | 0 | 0
| OfL | 13 |  | 1846115 | 1779468.875 | 1835242.375 | 1771809.5 | 1736744 | 1812517 | 1753513.125 | 1721284.875 | 405.2985 | 405.2985 | 405.2985 | 434.5369 | 434.5369 | 434.5369 | CZ13 | 164.4372 | 26.8262 | 269.853 | 77.3191 | 287.2716 | [5 empty] | 156.509 | 243.0268 | 188.0835 | 262.2504 | 533.2781 | 505.0688 | 678.7822 | 617.7266 | 584.1791 | 658.8677 | 601.6908 | 570.2557 | 0.069601 | -0.359 | -0.12559 | -0.28902 | -0.085097 | 0.15064 | 0.23342 | 0.13158 | 0.20392 | 3658.5581 | 2243.8979 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4904 | 9.0268 | 9.0268 | 8.4194 | 8.4194 |  | 0 | 0 | 0 | 0
| OfL | 14 |  | 1853594.125 | 1781529.625 | 1852394 | 1786588.875 | 1750221.125 | 1827628.875 | 1766305.75 | 1732262.25 | 427.5607 | 427.5607 | 427.5607 | 431.3226 | 431.3226 | 431.3226 | CZ14 | 168.548 | 2.8069 | 241.7739 | 60.1991 | 281.3019 | [5 empty] | 153.9083 | 238.9669 | 199.5913 | 278.5195 | 522.6467 | 491.177 | 686.7355 | 623.8884 | 589.3152 | 675.8004 | 615.2073 | 581.7066 | 0.073603 | -0.38378 | -0.15593 | -0.35508 | -0.13693 | 0.14699 | 0.22785 | 0.14048 | 0.21815 | 4681.5283 | 2918.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1245 | 10.9494 | 10.9494 | 10.8539 | 10.8539 |  | 0 | 0 | 0 | 0
| OfL | 15 |  | 2148958 | 1998094.375 | 2104329.25 | 1994615.75 | 1934245.25 | 2047599 | 1948247.75 | 1893685.25 | 502.0965 | 502.0965 | 502.0965 | 507.9604 | 507.9604 | 507.9604 | CZ15 | 300.4674 | 88.8848 | 427.6324 | 199.5411 | 502.5445 | [5 empty] | 218.5108 | 338.7476 | 307.271 | 414.6858 | 579.7179 | 529.7973 | 760.0823 | 684.9832 | 643.7446 | 712.952 | 646.7087 | 610.2761 | 0.099424 | -0.35922 | -0.12752 | -0.26229 | -0.060159 | 0.14957 | 0.2317 | 0.13041 | 0.20213 | 1085.7515 | 496.75 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1731 | 2.1624 | 2.1624 | 2.1375 | 2.1375 |  | 0 | 0 | 0 | 0
| OfL | 16 |  | 1681181.625 | 1639278 | 1706954.375 | 1668351.75 | 1646619.5 | 1685797.5 | 1650186.75 | 1629941.375 | 332.3563 | 332.3563 | 330.5203 | 334.33 | 334.33 | 334.3302 | CZ16 | 126.0804 | -77.5455 | 104.5688 | -13.8063 | 153.2624 | [5 empty] | 116.1483 | 182.5451 | 169.7952 | 230.3501 | 467.7195 | 443.6242 | 511.711 | 481.5192 | 465.1384 | 503.0822 | 473.6687 | 457.3015 | 0.072498 | -0.13236 | 0.0078091 | -0.10577 | 0.031161 | 0.090842 | 0.14091 | 0.087978 | 0.13693 | 11781.5194 | 8668.6176 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3662 | 35.4485 | 35.6454 | 35.2392 | 35.2392 |  | 0 | 0 | 0 | 0
|  |  |  | Baseline is FPFC w/ T-24 Chlr and Blr | [8 empty] | Baseline is T24 Heat Pump VRF System | [10 empty] | Baseline is T24 Heat Recovery VRF System
-77.5455
502.5445
-0.49501
0.26986
35.6454

## Htl_Svgs
|  |  |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 25 | 25 | 25 | 25 | 25 | 25 | [15 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [9 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  |  |  | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | kWhTotal | CoolCap | CoolCap | CoolCap | CoolCap | CoolCap | CoolCap |  |  | Baseline is FPFC w/ T-24 Chlr and Blr |  |  |  |  | Baseline is 2 Speed T-24 AC/Furnace, |  |  |  | Baseline is T24 Heat Pump VRF System |  |  |  | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer | kWPkPer |  | Baseline is FPFC w/ T-24 Chlr and Blr |  |  |  | Baseline is T24 Single-Mode VRF System, |  |  |  | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating | ThermHeating |  | Baseline is One Speed T-24 AC/Furnace, |  |  |  |  | Baseline is T24 Single-Mode VRF System,
|  |  | Sys ID | FPFC_1 | FPFC_2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 | [7 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | Baseline is T24 Heat Recovery VRF System |  | FPFC_1 | FPFC_2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 | [5 empty] | 14 | tons/system |  |  | FPFC_1 | FPFC_2 | VRF_HP_OAU0 | VRF_HP_OAU1 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU1 | VRF_HR_OAU2 |  | < 65 kBtuh |  |  |  |  | 14 | tons/system
Run ID | Bldg | CZ | [15 empty] | CZ | Hi Eff FPFC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 |  | VRF HP Std | VRF HP Tier2 | VRF HR Std | VRF HR Tier2 | VRF HP Tier1 | VRF HP Tier2 | VRF HR Tier1 | VRF HR Tier2 | [8 empty] | Hi Eff FPFC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP Tier1 | VRF HP Tier2 | VRF HR Tier1 | VRF HR Tier2 | [8 empty] | Hi Eff FPFC | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | 0 | VRF HP Tier1 | VRF HP Tier2 | VRF HR Tier1 | VRF HR Tier2
| Htl | 1 |  | 3048060.75 | 2955900.1372 | 3981387.5 | 3839662.75 | 3723684 | 3842653 | 3713791 | 3607963.5 | 438.17 | 438.1687 | 438.1674 | 436.3949 | 436.3919 | 436.389 | CZ01 | 210.3307 | -2130.0564 | -1541.9294 | -1820.81 | -1283.0358 | [5 empty] | 323.4479 | 588.1393 | 613.2022 | 855.7135 | 458.7003 | 424.276 | 440.3357 | 424.7982 | 413.1888 | 435.3592 | 420.6089 | 409.9117 | 0.078564 | 0.041912 | 0.10387 | 0.053486 | 0.1118 | 0.03546 | 0.061955 | 0.0338 | 0.058314 | 179925.8522 | 153660.5896 | 0 | 0 | 0 | 0 | 0 | 0 | 59.9431 | 410.6303 | 410.6326 | 412.3005 | 412.3061 |  | 0 | 0 | 0 | 0
| Htl | 2 |  | 3623069.5 | 3494826.75 | 4052447.5 | 3891685.5 | 3763636.75 | 3926173.25 | 3776112.5 | 3656588.25 | 617.2584 | 617.2583 | 617.2581 | 614.3523 | 613.6558 | 612.5861 | CZ02 | 207.7618 | -695.6211 | -227.7285 | -493.3713 | -54.7168 | [5 empty] | 260.4453 | 467.893 | 450.3095 | 646.21 | 669.7245 | 622.5062 | 845.901 | 775.3184 | 720.9396 | 827.0341 | 756.2947 | 704.3146 | 0.076497 | -0.28542 | -0.082972 | -0.25606 | -0.056466 | 0.11435 | 0.20245 | 0.11528 | 0.20033 | 143186.4525 | 116237.1584 | 0 | 0 | 0 | 0 | 0 | 0 | 43.6597 | 231.9716 | 231.9718 | 233.069 | 233.741 |  | 0 | 0 | 0 | 0
| Htl | 3 |  | 3378867.75 | 3280103 | 3664908.5 | 3549787.25 | 3457756 | 3563423.5 | 3454070.25 | 3368493 | 528.6225 | 528.6219 | 528.6216 | 524.2825 | 524.2821 | 524.2816 | CZ03 | 186.8342 | -541.1059 | -149.2339 | -352.0159 | 19.7885 | [5 empty] | 217.7762 | 391.873 | 402.1466 | 565.3746 | 556.67 | 520.6327 | 590.1246 | 553.4656 | 524.8334 | 570.4153 | 537.048 | 512.4104 | 0.068172 | -0.063286 | 0.060226 | -0.026217 | 0.084419 | 0.069348 | 0.12351 | 0.063644 | 0.11064 | 125886.2592 | 102857.0522 | 0 | 0 | 0 | 0 | 0 | 0 | 43.5646 | 238.1402 | 238.1406 | 240.1115 | 240.1119 |  | 0 | 0 | 0 | 0
| Htl | 4 |  | 3604455 | 3470811.75 | 3904156.75 | 3762466.25 | 3649118.5 | 3807330.25 | 3673781.75 | 3568011 | 587.4058 | 587.4036 | 587.4014 | 584.3076 | 584.3043 | 584.301 | CZ04 | 227.5144 | -510.2125 | -76.0357 | -347.2063 | 62.372 | [5 empty] | 241.2149 | 434.1806 | 394.2723 | 575.2955 | 638.3967 | 594.9582 | 774.0236 | 710.2145 | 665.2898 | 744.9257 | 688.3589 | 645.2029 | 0.07395 | -0.23089 | -0.045783 | -0.18232 | -0.011648 | 0.10863 | 0.18511 | 0.09681 | 0.17067 | 122173.6038 | 98039.337 | 0 | 0 | 0 | 0 | 0 | 0 | 41.0862 | 207.9884 | 207.99 | 209.0913 | 209.0936 |  | 0 | 0 | 0 | 0
| Htl | 5 |  | 3286392 | 3190901.5 | 3760854.75 | 3636325.5 | 3536370.75 | 3648833.75 | 3534305.75 | 3443263 | 496.9476 | 496.9455 | 496.9434 | 493.6363 | 493.6335 | 493.6307 | CZ05 | 192.154 | -954.754 | -503.0326 | -734.2284 | -317.7902 | [5 empty] | 250.5893 | 451.7295 | 458.9417 | 643.3793 | 522.9859 | 488.3011 | 541.9229 | 511.8399 | 489.9726 | 525.9209 | 498.0431 | 477.8394 | 0.069796 | -0.038107 | 0.066433 | -0.0059457 | 0.091458 | 0.060536 | 0.10454 | 0.056475 | 0.097404 | 135639.511 | 112956.7437 | 0 | 0 | 0 | 0 | 0 | 0 | 45.6442 | 272.9453 | 272.9476 | 274.7762 | 274.7793 |  | 0 | 0 | 0 | 0
| Htl | 6 |  | 3668484 | 3525176.5 | 3586188.5 | 3473885.75 | 3386339.25 | 3499994.5 | 3399312 | 3320872.5 | 563.8582 | 563.8579 | 563.8579 | 561.581 | 561.5817 | 561.5811 | CZ06 | 254.1552 | 145.9507 | 500.3827 | 300.0271 | 618.9872 | [5 empty] | 199.1685 | 354.4319 | 332.7681 | 472.4447 | 603.1594 | 563.4849 | 661.5298 | 614.8466 | 580.7201 | 644.6546 | 599.5163 | 566.535 | 0.070363 | -0.10352 | 0.039796 | -0.07389 | 0.065217 | 0.082793 | 0.14332 | 0.080377 | 0.13911 | 88235.7453 | 69887.8464 | 0 | 0 | 0 | 0 | 0 | 0 | 32.5399 | 156.4857 | 156.4858 | 157.1202 | 157.1202 |  | 0 | 0 | 0 | 0
| Htl | 7 |  | 3619428.5 | 3469502.25 | 3404922.5 | 3311787.5 | 3240294.25 | 3338953 | 3252381.5 | 3186567.5 | 539.38 | 539.38 | 539.38 | 536.6749 | 536.6749 | 536.6749 | CZ07 | 277.9603 | 397.6899 | 702.9075 | 522.6172 | 806.5609 | [5 empty] | 172.6705 | 305.2176 | 284.2335 | 406.8664 | 565.3547 | 531.3513 | 586.3513 | 550.5527 | 523.8713 | 573.1324 | 538.9573 | 513.835 | 0.063042 | -0.038927 | 0.076909 | -0.014492 | 0.095998 | 0.06637 | 0.11584 | 0.063679 | 0.11049 | 66736.0205 | 53330.9491 | 0 | 0 | 0 | 0 | 0 | 0 | 24.8527 | 123.7273 | 123.7273 | 124.3509 | 124.3509 |  | 0 | 0 | 0 | 0
| Htl | 8 |  | 3858038 | 3689526.75 | 3653933.75 | 3529140.5 | 3432986.5 | 3575003.5 | 3458398.5 | 3369451 | 638.016 | 638.0161 | 638.0161 | 637.9255 | 637.9255 | 637.9255 | CZ08 | 264.1176 | 319.9046 | 666.2081 | 443.6796 | 765.8998 | [5 empty] | 195.5958 | 346.3036 | 306.5174 | 445.9498 | 655.545 | 609.803 | 781.0082 | 717.6024 | 669.9186 | 760.9274 | 698.9775 | 653.9363 | 0.071694 | -0.19665 | -0.022528 | -0.1652 | 0.0025218 | 0.09938 | 0.17412 | 0.097111 | 0.16772 | 77633.4541 | 60974.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 26.1111 | 121.6795 | 121.6795 | 121.6967 | 121.6967 |  | 0 | 0 | 0 | 0
| Htl | 9 |  | 4022720 | 3796908.75 | 3819061 | 3675679 | 3565062.25 | 3740948.25 | 3604181.25 | 3499637.5 | 702.9331 | 702.9331 | 702.9331 | 698.8077 | 698.8077 | 698.8077 | CZ09 | 321.2414 | 289.7274 | 651.0687 | 403.2179 | 748.5357 | [5 empty] | 203.9767 | 361.3413 | 307.4948 | 457.0979 | 736.0905 | 682.8291 | 960.8306 | 873.3163 | 807.2155 | 925.9567 | 843.2548 | 780.8423 | 0.07577 | -0.31972 | -0.10118 | -0.2717 | -0.06404 | 0.1245 | 0.21853 | 0.11835 | 0.20766 | 83102.0749 | 67013.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8871 | 118.2219 | 118.2219 | 118.9198 | 118.9198 |  | 0 | 0 | 0 | 0
| Htl | 10 |  | 4010517 | 3821768.75 | 3956137.5 | 3795329.5 | 3670392.5 | 3866708 | 3713750.5 | 3596485.75 | 675.9191 | 675.9197 | 675.9197 | 673.239 | 673.239 | 673.239 | CZ10 | 279.2468 | 80.4527 | 503.2025 | 213.6076 | 614.984 | [5 empty] | 237.9099 | 422.7499 | 360.0311 | 534.2111 | 747.2887 | 694.0917 | 1076.2277 | 967.8876 | 886.3603 | 1041.4476 | 939.3483 | 862.931 | 0.078703 | -0.48665 | -0.20575 | -0.43693 | -0.17177 | 0.16029 | 0.2809 | 0.15165 | 0.26516 | 93483.4278 | 73742.249 | 0 | 0 | 0 | 0 | 0 | 0 | 29.2064 | 138.3057 | 138.3055 | 138.8562 | 138.8562 |  | 0 | 0 | 0 | 0
| Htl | 11 |  | 4055676.75 | 3861678.5 | 4369382 | 4159700 | 3997685 | 4257311 | 4056874.25 | 3902098.75 | 726.6485 | 726.6485 | 726.6487 | 729.0409 | 729.762 | 729.762 | CZ11 | 266.9767 | -431.7153 | 79.8071 | -276.5747 | 210.4494 | [5 empty] | 288.5604 | 511.5223 | 428.2324 | 640.3228 | 732.6119 | 671.3467 | 1004.489 | 907.9666 | 835.7545 | 981.4542 | 889.4972 | 819.2943 | 0.084312 | -0.37415 | -0.14194 | -0.34133 | -0.11878 | 0.13283 | 0.23221 | 0.12601 | 0.22221 | 121642.2298 | 99235.7581 | 0 | 0 | 0 | 0 | 0 | 0 | 30.8354 | 167.4017 | 167.4017 | 166.8524 | 166.6875 |  | 0 | 0 | 0 | 0
| Htl | 12 |  | 3976225 | 3796598.25 | 4132330.5 | 3957195 | 3819950.25 | 4022644.25 | 3856527.5 | 3726462 | 690.1059 | 690.1059 | 690.1061 | 686.6436 | 686.9309 | 686.9309 | CZ12 | 260.2887 | -226.2051 | 226.4503 | -67.6031 | 363.5926 | [5 empty] | 253.7806 | 452.6554 | 401.5003 | 590.8433 | 721.208 | 667.4831 | 907.0268 | 826.3005 | 764.7094 | 873.8115 | 798.3113 | 741.4512 | 0.07785 | -0.26926 | -0.063036 | -0.22225 | -0.029469 | 0.11698 | 0.20623 | 0.10991 | 0.19268 | 126356.2138 | 101005.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 36.7342 | 183.0969 | 183.0968 | 184.0201 | 183.9431 |  | 0 | 0 | 0 | 0
| Htl | 13 |  | 4071144 | 3878770.75 | 4321205 | 4115847.5 | 3958058 | 4206312 | 4010617 | 3861139.25 | 688.1481 | 688.1481 | 688.1484 | 682.4377 | 682.4377 | 682.8598 | CZ13 | 279.5521 | -363.3825 | 164.3338 | -198.0664 | 307.5371 | [5 empty] | 298.4205 | 527.7161 | 455.1155 | 673.7339 | 716.0414 | 666.5999 | 916.6836 | 833.8052 | 770.8766 | 890.2174 | 811.9958 | 752.295 | 0.071847 | -0.29157 | -0.079685 | -0.25523 | -0.053091 | 0.12044 | 0.21188 | 0.11462 | 0.20198 | 110318.5715 | 89125.161 | 0 | 0 | 0 | 0 | 0 | 0 | 30.7977 | 160.3122 | 160.3122 | 161.6537 | 161.5538 |  | 0 | 0 | 0 | 0
| Htl | 14 |  | 3993126.5 | 3796550.25 | 4450075 | 4234600.5 | 4066605 | 4302436.5 | 4100431 | 3943810 | 693.8752 | 693.875 | 693.8753 | 687.7518 | 687.0293 | 686.8285 | CZ14 | 283.302 | -658.5456 | -105.8958 | -449.7407 | 71.8032 | [5 empty] | 310.5379 | 552.6497 | 508.9215 | 737.1055 | 720.6107 | 660.2393 | 969.8849 | 881.8231 | 815.5021 | 953.0786 | 865.8883 | 800.2811 | 0.087006 | -0.35925 | -0.13676 | -0.33801 | -0.116 | 0.12691 | 0.22249 | 0.12691 | 0.22247 | 129295.7286 | 105983.703 | 0 | 0 | 0 | 0 | 0 | 0 | 33.5969 | 186.3386 | 186.3386 | 187.9977 | 188.2504 |  | 0 | 0 | 0 | 0
| Htl | 15 |  | 5113226 | 4597772 | 4788531 | 4507421.5 | 4294308 | 4651532 | 4387135.5 | 4186869.5 | 824.6589 | 824.6589 | 824.6589 | 836.9581 | 836.9581 | 836.9581 | CZ15 | 625.0511 | 393.7325 | 993.0384 | 551.6334 | 1106.8135 | [5 empty] | 340.8797 | 599.3059 | 479.5885 | 718.8669 | 840.5673 | 744.433 | 1150.7415 | 1036.9456 | 950.6299 | 1101.6143 | 994.0775 | 912.9232 | 0.11657 | -0.37612 | -0.13346 | -0.3119 | -0.086451 | 0.13799 | 0.24266 | 0.12849 | 0.22545 | 49923.0259 | 38916.1856 | 0 | 0 | 0 | 0 | 0 | 0 | 13.3471 | 60.5378 | 60.5378 | 59.6482 | 59.6482 |  | 0 | 0 | 0 | 0
| Htl | 16 |  | 3379882 | 3277688.5 | 4623747.5 | 4416527 | 4247984.5 | 4468652 | 4275192.5 | 4117854.5 | 596.5967 | 596.5938 | 596.5909 | 591.0498 | 591.0415 | 591.0341 | CZ16 | 171.2941 | -2084.9353 | -1455.1052 | -1842.0951 | -1248.6125 | [5 empty] | 347.3394 | 629.8504 | 589.7302 | 855.9456 | 577.8195 | 534.4556 | 635.8603 | 591.6698 | 561.0098 | 617.594 | 579.6564 | 551.2182 | 0.072685 | -0.097287 | 0.028176 | -0.067295 | 0.045008 | 0.074071 | 0.12546 | 0.064188 | 0.1123 | 211497.5949 | 180623.5443 | 0 | 0 | 0 | 0 | 0 | 0 | 51.7503 | 354.5068 | 354.5103 | 357.8338 | 357.8433 |  | 0 | 0 | 0 | 0
|  |  |  | Baseline is FPFC w/ T-24 Chlr and Blr | [8 empty] | Baseline is T24 Heat Pump VRF System | [10 empty] | Baseline is T24 Heat Recovery VRF System
-2130.0564
1106.8135
-0.48665
0.2809
412.3061

## OfS_Src
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25
|  |  |  | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | CoolCap
|  |  | Sys ID | AC_SHi | AC_EHi | PVAV_Std | PVAV_Hi | VRF_HP_OAU0 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU2 | VRF_HR_OAU0 |  | Comp to AC_SHi (lt 65, 2 spd) |  |  |  | Comp to AC_EHi (65 to 135 kBtuh, 2 spd) |  |  |  | Comp to AC_EHi (65 to 135 kBtuh, 2 spd)
Run ID | Bldg | CZ | [10 empty] | CZ | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2
| OfS | 1 |  | 85.2868 | 95.5335 | 108.1502 | 87.6702 | 90.791 | 80.1211 | 83.9577 | 74.3157 | 15.9207 | CZ01 | -0.34572 | 0.32446 | 0.083479 | 0.68911 | 0.29788 | 0.96807 | 0.72709 | 1.3327 | -0.19602 | 0.47417 | 0.23318 | 0.83881
| OfS | 2 |  | 111.6035 | 134.0835 | 166.4513 | 132.6371 | 139.6147 | 118.1363 | 130.3366 | 111.0162 | 20.6597 | CZ02 | -1.3558 | -0.31621 | -0.90675 | 0.028427 | -0.26773 | 0.7719 | 0.18136 | 1.1165 | -0.33774 | 0.70189 | 0.11135 | 1.0465
| OfS | 3 |  | 75.7641 | 94.6722 | 119.5226 | 96.7336 | 107.6795 | 92.3888 | 100.9875 | 87.3891 | 18.9088 | CZ03 | -1.6879 | -0.8792 | -1.334 | -0.6148 | -0.68789 | 0.12076 | -0.33398 | 0.38517 | -0.57887 | 0.22978 | -0.22497 | 0.49419
| OfS | 4 |  | 105.2631 | 130.1384 | 169.7524 | 135.363 | 142.7727 | 120.1025 | 134.9912 | 113.9265 | 19.9351 | CZ04 | -1.8816 | -0.74438 | -1.4912 | -0.43458 | -0.63377 | 0.50343 | -0.24343 | 0.81323 | -0.37169 | 0.76551 | 0.01865 | 1.0753
| OfS | 5 |  | 74.0005 | 91.9984 | 126.6536 | 102.7974 | 105.6491 | 90.6728 | 98.7052 | 85.3268 | 17.5859 | CZ05 | -1.7997 | -0.94805 | -1.4048 | -0.64405 | -0.77623 | 0.075373 | -0.38137 | 0.37937 | -0.16216 | 0.68945 | 0.2327 | 0.99344
| OfS | 6 |  | 107.2267 | 134.5885 | 183.2421 | 146.7574 | 147.5955 | 123.8236 | 137.2889 | 115.5014 | 22.0213 | CZ06 | -1.8332 | -0.75368 | -1.3651 | -0.37576 | -0.59066 | 0.48884 | -0.12263 | 0.86676 | -0.03806 | 1.0414 | 0.42997 | 1.4194
| OfS | 7 |  | 92.8901 | 119.6459 | 164.135 | 132.8194 | 141.1134 | 118.3997 | 132.7908 | 111.8013 | 21.5211 | CZ07 | -2.2407 | -1.1853 | -1.854 | -0.87872 | -0.99751 | 0.057908 | -0.61079 | 0.36451 | -0.38539 | 0.67003 | 0.0013284 | 0.97663
| OfS | 8 |  | 123.5265 | 154.5726 | 204.6266 | 163.309 | 169.2613 | 140.8253 | 158.401 | 132.2816 | 23.3846 | CZ08 | -1.9558 | -0.73975 | -1.4913 | -0.3744 | -0.62813 | 0.58788 | -0.16371 | 0.95323 | -0.25454 | 0.96147 | 0.20988 | 1.3268
| OfS | 9 |  | 135.7233 | 168.9739 | 211.4939 | 170.9215 | 183.897 | 152.9487 | 172.3427 | 143.9048 | 26.9784 | CZ09 | -1.7856 | -0.63849 | -1.3574 | -0.30326 | -0.55315 | 0.594 | -0.12487 | 0.92923 | -0.48096 | 0.66619 | -0.052677 | 1.0014
| OfS | 10 |  | 143.6804 | 176.7074 | 227.7991 | 181.7857 | 192.0798 | 158.7959 | 180.6128 | 149.7489 | 24.1714 | CZ10 | -2.0023 | -0.62535 | -1.5279 | -0.25106 | -0.63597 | 0.74102 | -0.16157 | 1.1153 | -0.42588 | 0.95111 | 0.048523 | 1.3254
| OfS | 11 |  | 173.0274 | 205.6917 | 249.195 | 198.298 | 206.1444 | 170.6508 | 194.6036 | 161.3111 | 24.1725 | CZ11 | -1.37 | 0.098315 | -0.89259 | 0.48469 | -0.018727 | 1.4496 | 0.45871 | 1.836 | -0.3246 | 1.1437 | 0.15284 | 1.5301
| OfS | 12 |  | 144.0493 | 172.5389 | 206.9069 | 165.6333 | 174.102 | 145.3238 | 163.1719 | 136.54 | 23.9386 | CZ12 | -1.2554 | -0.053241 | -0.79882 | 0.31369 | -0.065294 | 1.1369 | 0.39129 | 1.5038 | -0.35377 | 0.8484 | 0.10282 | 1.2153
| OfS | 13 |  | 174.6815 | 208.8977 | 251.8511 | 201.2376 | 211.2611 | 174.7915 | 198.173 | 164.2788 | 25.6832 | CZ13 | -1.4243 | -0.0042807 | -0.91466 | 0.40504 | -0.092022 | 1.328 | 0.41757 | 1.7373 | -0.39027 | 1.0297 | 0.11932 | 1.439
| OfS | 14 |  | 176.2685 | 209.7511 | 257.6143 | 204.5558 | 214.3135 | 177.1244 | 200.3248 | 165.7059 | 24.6989 | CZ14 | -1.5404 | -0.034652 | -0.97398 | 0.42766 | -0.18472 | 1.321 | 0.38165 | 1.7833 | -0.39507 | 1.1106 | 0.1713 | 1.5729
| OfS | 15 |  | 265.9342 | 323.9745 | 411.3159 | 327.8233 | 339.0153 | 274.9685 | 317.1445 | 257.8996 | 30.9084 | CZ15 | -2.3644 | -0.29229 | -1.6568 | 0.25995 | -0.48662 | 1.5855 | 0.22097 | 2.1378 | -0.3621 | 1.71 | 0.3455 | 2.2623
| OfS | 16 |  | 185.0979 | 205.4304 | 215.0215 | 175.6946 | 174.4556 | 148.5857 | 159.6832 | 136.2443 | 20.3699 | CZ16 | 0.52245 | 1.7925 | 1.2477 | 2.3983 | 1.5206 | 2.7906 | 2.2458 | 3.3965 | 0.060824 | 1.3308 | 0.78604 | 1.9367
AC/furnace, 2 spd, lt 65 kBtuh
AC/furnace, 2 spd, 65 to 135 kBtuh
PVAV/Gas Boiler

## EPr_Src
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25
|  |  |  | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | CoolCap
|  |  | Sys ID | AC_SHi | AC_EHi | PVAV_Std | PVAV_Hi | VRF_HP_OAU0 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU2 | VRF_HR_OAU0 |  | Comp to AC_SHi (lt 65, 2 spd) |  |  |  | Comp to AC_EHi (65 to 135 kBtuh, 2 spd) |  |  |  | Comp to AC_EHi (65 to 135 kBtuh, 2 spd)
Run ID | Bldg | CZ | [10 empty] | CZ | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2
| EPr | 1 |  | 1726.7036 | 1762.1851 | 1849.9761 | 1737.3899 | 1028.9476 | 911.9912 | 940.108 | 836.5589 | 76.0791 | CZ01 | 9.1715 | 10.7088 | 10.3392 | 11.7003 | 9.6378 | 11.1751 | 10.8056 | 12.1666 | 9.3119 | 10.8492 | 10.4796 | 11.8407
| EPr | 2 |  | 1378.6782 | 1483.5428 | 1539.4395 | 1405.1715 | 1051.4601 | 927.1751 | 966.7046 | 856.3698 | 115.4886 | CZ02 | 2.8333 | 3.9095 | 3.5672 | 4.5226 | 3.7413 | 4.8175 | 4.4752 | 5.4306 | 3.0627 | 4.1389 | 3.7966 | 4.752
| EPr | 3 |  | 1153.6782 | 1221.8139 | 1304.5657 | 1214.5341 | 832.5276 | 748.2732 | 773.9375 | 698.9151 | 99.9922 | CZ03 | 3.2118 | 4.0544 | 3.7977 | 4.548 | 3.8932 | 4.7358 | 4.4791 | 5.2294 | 3.8204 | 4.663 | 4.4063 | 5.1566
| EPr | 4 |  | 1141.7363 | 1240.6866 | 1352.5996 | 1225.6179 | 946.2597 | 837.4283 | 878.4584 | 780.8468 | 108.2971 | CZ04 | 1.805 | 2.8099 | 2.4311 | 3.3324 | 2.7187 | 3.7236 | 3.3448 | 4.2461 | 2.5796 | 3.5845 | 3.2056 | 4.107
| EPr | 5 |  | 1186.7855 | 1253.9044 | 1380.8142 | 1278.0661 | 859.2575 | 768.6562 | 798.6957 | 717.5751 | 89.7434 | CZ05 | 3.6496 | 4.6592 | 4.3244 | 5.2284 | 4.3975 | 5.4071 | 5.0723 | 5.9763 | 4.6667 | 5.6763 | 5.3416 | 6.2455
| EPr | 6 |  | 944.225 | 1055.7148 | 1178.191 | 1065.3924 | 846.2176 | 754.8684 | 794.715 | 713.2021 | 117.229 | CZ06 | 0.83603 | 1.6153 | 1.2754 | 1.9707 | 1.7871 | 2.5663 | 2.2264 | 2.9217 | 1.8696 | 2.6489 | 2.309 | 3.0043
| EPr | 7 |  | 809.2462 | 916.5431 | 1010.9296 | 937.1071 | 769.322 | 695.851 | 726.6599 | 660.6608 | 135.3027 | CZ07 | 0.29507 | 0.83809 | 0.61038 | 1.0982 | 1.0881 | 1.6311 | 1.4034 | 1.8912 | 1.2401 | 1.7831 | 1.5554 | 2.0432
| EPr | 8 |  | 1004.8432 | 1160.876 | 1258.9816 | 1130.0033 | 957.5699 | 847.8487 | 893.8332 | 795.6231 | 154.7212 | CZ08 | 0.30554 | 1.0147 | 0.71748 | 1.3522 | 1.314 | 2.0232 | 1.726 | 2.3607 | 1.1145 | 1.8236 | 1.5264 | 2.1612
| EPr | 9 |  | 1088.2913 | 1263.909 | 1344.6007 | 1198.7865 | 1023.3671 | 900.1127 | 949.9286 | 840.2192 | 155.9981 | CZ09 | 0.41619 | 1.2063 | 0.88695 | 1.5902 | 1.542 | 2.3321 | 2.0127 | 2.716 | 1.1245 | 1.9146 | 1.5953 | 2.2985
| EPr | 10 |  | 1116.2375 | 1275.5598 | 1386.3121 | 1226.782 | 1056.4271 | 920.0494 | 984.6367 | 862.1519 | 124.9337 | CZ10 | 0.47874 | 1.5703 | 1.0534 | 2.0338 | 1.754 | 2.8456 | 2.3286 | 3.309 | 1.3636 | 2.4552 | 1.9382 | 2.9186
| EPr | 11 |  | 1491.2947 | 1648.0876 | 1756.3395 | 1570.0185 | 1209.9665 | 1049.9889 | 1122.3406 | 977.3597 | 120.2804 | CZ11 | 2.3389 | 3.669 | 3.0674 | 4.2728 | 3.6425 | 4.9725 | 4.371 | 5.5764 | 2.9934 | 4.3235 | 3.722 | 4.9273
| EPr | 12 |  | 1389.7461 | 1516.7797 | 1587.255 | 1430.7754 | 1102.6707 | 964.5868 | 1019.1417 | 896.1253 | 118.4049 | CZ12 | 2.4245 | 3.5907 | 3.13 | 4.1689 | 3.4974 | 4.6636 | 4.2028 | 5.2418 | 2.771 | 3.9372 | 3.4765 | 4.5154
| EPr | 13 |  | 1433.5471 | 1586.9993 | 1686.0059 | 1496.7958 | 1221.7635 | 1056.2815 | 1133.5623 | 984.5624 | 123.9684 | CZ13 | 1.7084 | 3.0432 | 2.4198 | 3.6218 | 2.9462 | 4.2811 | 3.6577 | 4.8596 | 2.2186 | 3.5534 | 2.93 | 4.132
| EPr | 14 |  | 1565.7481 | 1726.5685 | 1834.5707 | 1629.3837 | 1293.4788 | 1118.3338 | 1195.2449 | 1037.1516 | 132.4592 | CZ14 | 2.0555 | 3.3778 | 2.7971 | 3.9906 | 3.2696 | 4.5919 | 4.0112 | 5.2048 | 2.5359 | 3.8582 | 3.2775 | 4.4711
| EPr | 15 |  | 1429.7153 | 1724.8075 | 1970.4069 | 1650.4098 | 1629.3656 | 1369.137 | 1519.7941 | 1282.2599 | 151.6449 | CZ15 | -1.3166 | 0.39947 | -0.59401 | 0.97237 | 0.62938 | 2.3454 | 1.3519 | 2.9183 | 0.13877 | 1.8548 | 0.86133 | 2.4277
| EPr | 16 |  | 2300.9379 | 2359.0873 | 2407.9378 | 2222.236 | 1500.077 | 1307.42 | 1359.8656 | 1185.2591 | 91.8472 | CZ16 | 8.7195 | 10.8171 | 10.2461 | 12.1471 | 9.3526 | 11.4502 | 10.8792 | 12.7802 | 7.8626 | 9.9602 | 9.3892 | 11.2902
AC/furnace, 2 spd, lt 65 kBtuh
AC/furnace, 2 spd, 65 to 135 kBtuh
PVAV/Gas Boiler

## OfL_Src
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25
|  |  |  | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | CoolCap
|  |  | Sys ID | FPFC_1 | FPFC_2 |  |  | VRF_HP_OAU0 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU2 | VRF_HR_OAU0 |  | Comp to Std FPFC |  |  |  | Comp to Hi Effic FPFC |  |  |  | NA
Run ID | Bldg | CZ | [10 empty] | CZ | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2
| OfL | 1 |  | 2443.4871 | 1954.0628 |  |  | 1460.2922 | 1228.8531 | 1391.7117 | 1179.4408 | 285.878 | CZ01 | 3.4392 | 4.2488 | 3.6791 | 4.4216 | 1.7272 | 2.5368 | 1.9671 | 2.7096 | -5.1081 | -4.2985 | -4.8682 | -4.1257
| OfL | 2 |  | 3380.9087 | 2687.4487 |  |  | 2502.891 | 2003.2426 | 2383.7254 | 1918.1831 | 382.7056 | CZ02 | 2.2942 | 3.5998 | 2.6056 | 3.8221 | 0.48224 | 1.7878 | 0.79362 | 2.0101 | -6.54 | -5.2344 | -6.2286 | -5.0122
| OfL | 3 |  | 2847.1294 | 2286.658 |  |  | 2077.9288 | 1682.4373 | 1989.5949 | 1618.4223 | 345.4191 | CZ03 | 2.2269 | 3.3718 | 2.4826 | 3.5571 | 0.60428 | 1.7492 | 0.86001 | 1.9346 | -6.0157 | -4.8707 | -5.7599 | -4.6854
| OfL | 4 |  | 3346.7156 | 2696.1204 |  |  | 2617.6869 | 2085.983 | 2509.6759 | 2004.8165 | 351.4517 | CZ04 | 2.0743 | 3.5872 | 2.3817 | 3.8182 | 0.22317 | 1.736 | 0.5305 | 1.967 | -7.4482 | -5.9353 | -7.1409 | -5.7044
| OfL | 5 |  | 2741.2687 | 2213.56 |  |  | 2082.6863 | 1678.6887 | 1993.4282 | 1610.8318 | 305.3857 | CZ05 | 2.1566 | 3.4795 | 2.4488 | 3.7017 | 0.42855 | 1.7515 | 0.72083 | 1.9737 | -6.8199 | -5.4969 | -6.5276 | -5.2747
| OfL | 6 |  | 3312.1233 | 2696.1298 |  |  | 2825.6004 | 2232.6171 | 2650.3102 | 2104.7969 | 377.4116 | CZ06 | 1.2891 | 2.8603 | 1.7536 | 3.199 | -0.34305 | 1.2281 | 0.1214 | 1.5668 | -7.4868 | -5.9156 | -7.0223 | -5.5769
| OfL | 7 |  | 3230.1944 | 2655.0881 |  |  | 2719.4256 | 2153.164 | 2587.06 | 2054.5464 | 359.2355 | CZ07 | 1.4218 | 2.9981 | 1.7903 | 3.2726 | -0.1791 | 1.3972 | 0.18937 | 1.6717 | -7.57 | -5.9937 | -7.2016 | -5.7192
| OfL | 8 |  | 3546.6921 | 2907.1723 |  |  | 3117.8623 | 2444.7386 | 2945.1954 | 2326.1284 | 405.4829 | CZ08 | 1.0576 | 2.7176 | 1.4834 | 3.0101 | -0.5196 | 1.1405 | -0.093772 | 1.433 | -7.6893 | -6.0292 | -7.2634 | -5.7367
| OfL | 9 |  | 4097.0035 | 3283.9884 |  |  | 3323.2249 | 2611.1079 | 3095.4865 | 2448.8356 | 445.6552 | CZ09 | 1.7363 | 3.3342 | 2.2473 | 3.6983 | -0.088042 | 1.5099 | 0.42298 | 1.874 | -7.4569 | -5.859 | -6.9459 | -5.4949
| OfL | 10 |  | 3812.5612 | 3105.9788 |  |  | 3425.5318 | 2678.5153 | 3261.2861 | 2561.7753 | 421.426 | CZ10 | 0.91838 | 2.691 | 1.3081 | 2.968 | -0.75827 | 1.0143 | -0.36853 | 1.2913 | -8.1284 | -6.3558 | -7.7387 | -6.0788
| OfL | 11 |  | 4027.1241 | 3250.5074 |  |  | 3382.6632 | 2651.3477 | 3269.9987 | 2570.102 | 404.4992 | CZ11 | 1.5932 | 3.4012 | 1.8718 | 3.602 | -0.32671 | 1.4812 | -0.048186 | 1.6821 | -8.3626 | -6.5546 | -8.0841 | -6.3538
| OfL | 12 |  | 3816.6251 | 3058.3102 |  |  | 2998.3123 | 2371.9289 | 2838.068 | 2258.5062 | 420.6476 | CZ12 | 1.9454 | 3.4345 | 2.3263 | 3.7041 | 0.14263 | 1.6317 | 0.52358 | 1.9014 | -7.1278 | -5.6388 | -6.7469 | -5.3691
| OfL | 13 |  | 3907.0542 | 3184.9063 |  |  | 3500.7611 | 2736.4196 | 3324.4165 | 2616.459 | 434.5369 | CZ13 | 0.935 | 2.694 | 1.3408 | 2.97 | -0.72688 | 1.0321 | -0.32105 | 1.3082 | -8.0563 | -6.2973 | -7.6505 | -6.0213
| OfL | 14 |  | 4074.5017 | 3289.2729 |  |  | 3633.8627 | 2841.0069 | 3441.684 | 2701.6444 | 431.3226 | CZ14 | 1.0216 | 2.8598 | 1.4672 | 3.1829 | -0.79891 | 1.0393 | -0.35336 | 1.3624 | -8.4249 | -6.5867 | -7.9794 | -6.2636
| OfL | 15 |  | 5989.6494 | 4607.0535 |  |  | 5588.8731 | 4269.0254 | 5148.6441 | 3954.2785 | 507.9604 | CZ15 | 0.78899 | 3.3873 | 1.6557 | 4.0069 | -1.9329 | 0.66546 | -1.0662 | 1.2851 | -11.0026 | -8.4042 | -10.1359 | -7.7846
| OfL | 16 |  | 3463.7956 | 2814.3056 |  |  | 2505.2534 | 2037.0574 | 2341.078 | 1907.6348 | 334.33 | CZ16 | 2.8671 | 4.2675 | 3.3581 | 4.6546 | 0.92439 | 2.3248 | 1.4155 | 2.7119 | -7.4934 | -6.093 | -7.0023 | -5.7058
Comp to Std FPFC
Comp to Hi Effic FPFC

## Htl_Src
|  |  |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25
|  |  |  | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | MMBtuSrc | CoolCap
|  |  | Sys ID | FPFC_1 | FPFC_2 |  |  | VRF_HP_OAU0 | VRF_HP_OAU2 | VRF_HR_OAU0 | VRF_HR_OAU2 | VRF_HR_OAU0 |  | Comp to Std FPFC |  |  |  | Comp to Hi Effic FPFC |  |  |  | NA
Run ID | Bldg | CZ | [10 empty] | CZ | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2 | VRF HP T-24 | VRF HP Tier2 | VRF HR T-24 | VRF HR Tier2
| Htl | 1 |  | 24088.5418 | 20924.6922 |  |  | 13364.2007 | 11364.425 | 12287.6273 | 10466.435 | 436.3949 | CZ01 | 24.5749 | 29.1573 | 27.0418 | 31.2151 | 17.3249 | 21.9074 | 19.7919 | 23.9651 | -30.6241 | -26.0416 | -28.1571 | -23.9839
| Htl | 2 |  | 24837.2635 | 21061.1173 |  |  | 13915.6282 | 11674.4546 | 12935.7347 | 10843.7641 | 614.3523 | CZ02 | 17.7775 | 21.4255 | 19.3725 | 22.7776 | 11.6309 | 15.279 | 13.2259 | 16.6311 | -22.6509 | -19.0029 | -21.0559 | -17.6507
| Htl | 3 |  | 21230.03 | 18108.9655 |  |  | 10908.3258 | 9300.8271 | 10120.8036 | 8608.1441 | 524.2825 | CZ03 | 19.6873 | 22.7534 | 21.1894 | 24.0746 | 13.7343 | 16.8004 | 15.2364 | 18.1216 | -20.8062 | -17.7401 | -19.3041 | -16.4189
| Htl | 4 |  | 22581.8901 | 19041.2595 |  |  | 12764.8942 | 10785.7913 | 12013.5203 | 10156.4024 | 584.3076 | CZ04 | 16.8011 | 20.1882 | 18.087 | 21.2653 | 10.7415 | 14.1286 | 12.0275 | 15.2058 | -21.8462 | -18.4591 | -20.5603 | -17.3819
| Htl | 5 |  | 21488.639 | 18433.8255 |  |  | 11652.8675 | 9910.8793 | 10783.5827 | 9188.3577 | 493.6363 | CZ05 | 19.9251 | 23.454 | 21.6861 | 24.9177 | 13.7367 | 17.2656 | 15.4977 | 18.7293 | -23.6062 | -20.0773 | -21.8452 | -18.6136
| Htl | 6 |  | 19677.2683 | 16609.7281 |  |  | 10297.4586 | 8746.6253 | 9628.5939 | 8238.6091 | 561.581 | CZ06 | 16.7025 | 19.4641 | 17.8935 | 20.3687 | 11.2402 | 14.0017 | 12.4312 | 14.9063 | -18.3366 | -15.575 | -17.1455 | -14.6704
| Htl | 7 |  | 17147.7018 | 14520.4199 |  |  | 8890.8364 | 7613.3161 | 8378.9087 | 7196.3995 | 536.6749 | CZ07 | 15.3852 | 17.7657 | 16.3391 | 18.5425 | 10.4897 | 12.8702 | 11.4436 | 13.647 | -16.5665 | -14.1861 | -15.6126 | -13.4092
| Htl | 8 |  | 20075.2882 | 16948.1016 |  |  | 10823.1678 | 9108.6123 | 10210.6642 | 8615.5785 | 637.9255 | CZ08 | 14.5035 | 17.1912 | 15.4636 | 17.964 | 9.6013 | 12.289 | 10.5615 | 13.0619 | -16.9662 | -14.2785 | -16.006 | -13.5056
| Htl | 9 |  | 21900.6258 | 18320.4008 |  |  | 12104.5548 | 10133.5158 | 11498.3945 | 9625.8287 | 698.8077 | CZ09 | 14.0183 | 16.8388 | 14.8857 | 17.5653 | 8.8949 | 11.7155 | 9.7624 | 12.442 | -17.3217 | -14.5012 | -16.4543 | -13.7746
| Htl | 10 |  | 22829.356 | 19221.7202 |  |  | 13168.2643 | 10950.8843 | 12474.2895 | 10377.3597 | 673.239 | CZ10 | 14.3502 | 17.6438 | 15.381 | 18.4957 | 8.9915 | 12.2851 | 10.0223 | 13.137 | -19.5596 | -16.266 | -18.5288 | -15.4141
| Htl | 11 |  | 25979.9329 | 22071.9013 |  |  | 16375.0378 | 13490.6666 | 15505.3666 | 12748.9183 | 729.0409 | CZ11 | 13.1747 | 17.1311 | 14.3676 | 18.1485 | 7.8142 | 11.7706 | 9.0071 | 12.788 | -22.4611 | -18.5047 | -21.2682 | -17.4872
| Htl | 12 |  | 25878.29 | 21787.9486 |  |  | 14535.5247 | 12111.4554 | 13684.3598 | 11385.979 | 686.6436 | CZ12 | 16.5191 | 20.0495 | 17.7587 | 21.106 | 10.5621 | 14.0925 | 11.8017 | 15.149 | -21.169 | -17.6386 | -19.9294 | -16.5821
| Htl | 13 |  | 24973.3143 | 21167.0407 |  |  | 16001.184 | 13183.1708 | 15109.617 | 12431.0701 | 682.4377 | CZ13 | 13.1472 | 17.2765 | 14.4536 | 18.3786 | 7.5697 | 11.699 | 8.8762 | 12.8011 | -23.4471 | -19.3178 | -22.1407 | -18.2157
| Htl | 14 |  | 26294.9245 | 22301.6084 |  |  | 17001.2232 | 14025.4989 | 15855.5441 | 13072.6012 | 687.7518 | CZ14 | 13.5132 | 17.8399 | 15.179 | 19.2254 | 7.7068 | 12.0336 | 9.3727 | 13.4191 | -24.72 | -20.3933 | -23.0542 | -19.0077
| Htl | 15 |  | 26988.5245 | 21473.0988 |  |  | 19627.6391 | 15792.4669 | 18564.5179 | 14958.7431 | 836.9581 | CZ15 | 8.7948 | 13.3771 | 10.065 | 14.3732 | 2.205 | 6.7872 | 3.4752 | 7.7834 | -23.4512 | -18.8689 | -22.1809 | -17.8728
| Htl | 16 |  | 29802.7084 | 25888.3457 |  |  | 18348.9259 | 15432.9879 | 17145.3686 | 14423.1774 | 591.0498 | CZ16 | 19.3787 | 24.3122 | 21.415 | 26.0207 | 12.756 | 17.6895 | 14.7923 | 19.398 | -31.0446 | -26.1111 | -29.0083 | -24.4026
Comp to Std FPFC
Comp to Hi Effic FPFC